## Sheet1
Item
No. | ELECTRICAL INSTALLATION |  | Quantity | Rate | Amount
R
PREAMBLES
All equipment, electrical materials or methods of
installation shall comply fully with SANS 10142-1 as
published December 2001
SUPPLEMENTARY PREAMBLES
Proprietory items or materials
Proprietory items or materials where specified are to
be of the brand specified - or other approved - by the
Head: Works
CPAP WORK GROUP
Unless otherwise stated all items in this bill will be
Work Group 160
ELECTRICAL INSTALLATION
a) The overall completed electrical installation shall
comply fully with SANS 10142-1 "The Wiring of
Premises" and Telkom regulations where applicable.
SANS 10142-1 takes preference over any local
authority regulations pertaining to electrical installation
b) The equipment supplied and installed shall
comply in full with the requirements as set out in
clause 4 "Compliance" of SANS 10142-1.
c) All work must be carried out under full time
supervision of an Installation Electrician and the
statutory Certificate of Compliance, as per clause 8.8
of SANS 10142-1, shall be issued after completion to
the Department. Full particulars as requested under
clauses 8.8.1 and 8.8.2 must be indicated on the
Certificate of Compliance. The special Section 5 -
"Responsibility" of clause 8.8.1 must be completed in
full and duly signed off by the responsible persons and
the information required under 8.8.2
| Carried Forward to Collection Page |  |  | R
Electrical Installation
Item
No. | GUARANTEE |  | Quantity | Rate | Amount
R
1 | Guarantee the efficient and safe working of the
whole installation for 12 months after handover of
| the completed building to the Department. | Item
AS BUILT DRAWINGS
2 | Provision for the drawings showing all site cable
routes, conduit routes, draw boxes and positions
| of outlets etc. | Item
CERTIFICATE OF COMPLIANCE
3 | Provision for the Certificate of Compliance to be
issued on completion of the project in addition to the
| detailed testing specified | Item
LIGHT SWITCHES/SOCKET OUTLETS/ISOLATORS
4 | All light switches, switch socket outlets and cover
plates to be engraved with circuit numbers as per
| the distribution board layout drawings | Item
CONDUITS
The required solid conduit work shall comply fully
with the below quoted standards
a) Screwed metallic conduit and accessories:
SANS 162
b) Plain ended metallic conduit and accessories :
SANS 1007
c) Non metallic conduit : SANS 950
Non metalllic conduit shall be installed in accordance
with Appendix C of SANS 950 and shall not be
installed or used under the following conditions:
i) Outside a building (unless protected, or
sheltered under eaves)
ii) For mechanical load bearing
| Carried Forward to Collection Page |  |  | R
Electrical Installation
Item
No. |  |  | Quantity | Rate | Amount
| iii) Where they may be subjected to temperature |  |  |  | R
below -10oC or above 70oC for prolonged periods
iv) As primary electrical insulation
v) In areas where they may be subjected to
mechanical damage
vi) For applications other than for which they are
designed for
Only in very special circumstances and with prior
approval may shorter lengths of circuit wiring be
carried out in the approved unarmoured metal
sheathed cables or in copper braided cables
FIXING OF CONDUITS
The fixing of conduits shall be as follows
a) Build in conduits in wall chases with cement
mortar and clamps
b) Fix conduits on wall surfaces and in roof spaces
with approved saddles
c) Cast conduit in concrete surface beds or slabs
d) Do surface fixing level, plumb, neatly and in
straight line by means of standard spacer saddles
CHASING
All chasing shall be carried out neatly. Do not chase
walls constructed of hollow blocks, locate services
in the block cavities. Chase solid walls not deeper
than one third of the wall thickness vertically and not
more than one sixth horizontally. Avoid horizontal
chasing where possible. Ensure that chases, holes
and recesses are so made as not to impair the
strength or stability of the wall, or reduce the fire
resistance properties of the wall. Fill chases with
mortar once the conduits are in position
Chasing and making good have not been measured
separately and shall be deemed to be included in the
descriptions of conduiting
| Carried Forward to Collection Page |  |  | R
Electrical Installation
Item
No. | COPPER CONDUCTORS |  | Quantity | Rate | Amount
R
PVC insulated copper conductors shall conform
with SANS 150
ELECTRICAL CABLES
The PVC insulated 600/1000V grade cables shall be
manufactured in accordance with SANS 1507 and
shall be handled and installed in accordance with
SANS 0198 - "The Selection, Handling and Installation
of Electric Power Cables of rating not exceeding 33 kV"
LAYING OF ELECTRIC CABLES
Excavate 600 mm below finished ground level
Encase the installed cable in river sand or sifted sand
Mark the cable route with approved concrete cable
markers
ELECTRICAL DISTRIBUTION KIOSKS AND BOARDS
Under Annexure L of SANS 10142-1 it clearly states
that allowance must be made for the supply and
installation of approved Surge Protection Devices
(SPDs) into low voltage systems
.1 Distribution Kiosks
The kiosks shall have a weatherproof construction
complete with lockable doors and shall be of the
foundation mounted or root planted types. These
units shall be constructed from
1.1 Pre painted mild steel
1.2 3CR 12 (within 50 km of the coast and in
corrosive industrial atmospheres)
1.3 Fibreglass (within 50 km of the coast and in
corrosive industrial atmospheres)
1.4 The required surge protectoin devices that
need to be installed in a distribution kiosk shall
either be for a Zone LPZ O(A) OR LPZ O(B) with a
peak current rating of 100kA
| Carried Forward to Collection Page |  |  | R
Electrical Installation
Item
No. | .2 Distribution Boards |  | Quantity | Rate | Amount
R
The required pre painted 1.6 mm thick mild steel
boards shall either be of the flush, semi flush or
surface mounted types complete with lockable
doors. Each board shall be fitted with circuit
labelling and legend card installed in permanently
fixed steel type legend card holders
The general construction shall comply fully with
SANS 1180, Part 1 for flush type boards and Part 2
for the surface types
The specified equipment shall comply with the
following:
Moulded casse circuit breaker: SANS 156
On load isolators: SANS 152
Earth leakage relays: SANS 767
Surge Protection Units: SANS 61312-1 IEC 61312-1
Provision needs to be made for the required Zone
LPZ1 equipment with a peak current rating of 40 kA
any distribution board said sub-distribution board
shall be fitted with the required Zone LPZ2
equipment with a rating of 10kA
The internal power wiring shall comply fully with
600/1000V grade PVC insulated stranded
annealed copper conductors to SANS 1507
The final colour to the boards shall be determined
by the architect on site at a later stage. The paint
finishes shall be of a high quality paint applied
according to the best available method. Baked,
enamel, electro-statically applied powder coating or
similar proven methods shall be used. Painted
metal shall be corrosion resistant for a period of at
least 168 hours when tested in accordance with
SANS Methods 155.
The connected load to the boards shall be
balanced as equally as possible across
multi-phase supplies
Carried Forward to Collection Page
R
Electrical Installation
Item
No. | LIGHT SWITCHES |  | Quantity | Rate | Amount
R
Flush type
All flush type tumbler 16A, 220/250V light
switches complete with cover plate shall be
suitable for mounting inside standard type 100 x
50 mm wall boxes and shall comply fully with SANS
163 and shall further bear the mark
The dimmer type units shall comply with SANS 1012
Surface type
These units shall comply with SANS 163 and shall
be provided with specially manufactured surface
mounting type box
Watertight type
Watertight switches shall be of the micro graph
type suitable for surface mounting and shall bear
the SANS mark
The housing shall be of galvanised cast iron or die
cast aluminium with watertight cover plate and
toggle
The switches shall have a porcelain base and a
quick acting spring mechanism and further be
rated at 16A, 220/250V
Wall sockets
All switched and unswitched socket shall be of
the same manufacture and shall conform to SANS
164 and shall bear the SANS mark for normal use
under normal environmental conditions
Switches, when installed, shall be of the tumbler
operated micro graph type rated at 16A, 220/250V
Where 13A flat pin switched socket outlets are
specified, these shall comply with BS 1363
Carried Forward to Collection Page
R
Electrical Installation
Item
No. | EARTHING SYSTEM |  | Quantity | Rate | Amount
R
5 | Earthing of wash hand basin and all cold and hot
water piping, by means of standard copper tape earth
strapping at regular intervals of 6m and connecting
same to the electricla earth system at the distribution
| board (6 No wash hand basins ) | Item
SUNDRIES
Bonding
6 | The overall bonding of the completed electrical
installation shall be carried out and tested as
specified under Clause 6.13 of SANS 0142-1
| Allow for bonding and testing thereof | Item
Testing and commissioning
7 | Allow for testing and commissioning the whole of the
electrical installation as laid down in the specification
and for re-testing as may be required after the making
good of all defective work to the entire satisfaction of
| the Department and the Engineer | Item
LIGHT FITTING LUMINAIRES
All installed light fitting luminaires and its associated
equipment shall comply fully with SANS approved
equipment or materials as applicable from the 1st
January 1997
TESTING
8 | After the installation has been completed the Electrical
| Contractor shall issue a certificate of compliance | Item
9 | Before issuing a certificate of compliance, an
acredited person shall inspect and test each new
installation or extension of an existing installatoin
| for compliance with the relevant standard | Item
Carried Forward to Collection Page
R
Electrical Installation
Item
No. | SCHEDULES |  | Quantity | Rate | Amount
R
MOUNTING HEIGHTS OF OUTLETS
All electrical outlets shall be installed at the below listed
heights if not specified in the symbols list on the drawings:
Socket outlets: as specified on drawings
External wall light: 2000 mm above finished level
Light switches: 1400 mm (to centre of box) above
finished floor level
Distribution board: 1800 mm to top edge of board
LIGHT FITTING SCHEDULE
Light fittings supplied and installed shall be similar
and equal approved to the specified equipment. The
light fittings shall further comply in full with the
standards and specifications applicable to all
materials and components of the specified equipment
Prior approval of alternative type of fittings must
first be obtained in writing before submitting a
tender offer based on the alternative types
10 | P&Gs | Item
DISTRIBUTION BOARDS
Distribution boards complete with sheetmetal trays,
frames, subframes, busbars, provision for four
future circuit breakers, labeling and legend cards
11 | Typical distribution board as per single line
drawing 19023_02_400, supplied complete with
detailed shop drawing and specification including
| circuit breakers, Earth & Neutral busbars. | No. | 6
12 | 40A CBI / HYMAG SX1-G3 single pole 230 V
circuit breaker 5 kA fault level installed in
| existing distribution board | No. | 1
13 | Allow to work on existing distribution board and
| update legend card | Item
| Carried Forward to Collection Page |  |  | R
Electrical Installation
Item
No. |  |  | Quantity | Rate | Amount
DISTRIBUTION CABLES
600/1000V rated cables laid in ground or in sleeves. To be
protected when installed vertically up wall from ground
14 | 16mm² 2 core PVC/SWA/ECC/PVC cable | m | 67
15 | Termination for 16 mm² 2 core cable above | No. | 6
16 | 10mm² 2 core PVC/SWA/ECC/PVC cable | m | 33
17 | Termination for 10 mm² 2 core cable above | No. | 2
18 | 6mm² 2 core PVC/SWA/ECC/PVC cable | m | 29
19 | Termination for 6 mm² 2 core cable above | No. | 2
EXCAVATION
20 | Excavate for and build cable inspection chamber with
half brick sides fitted with 600 x 600 x 600 medium
duty cover and frame complete with drain holes. Size
| internally 600 x 600 x 600 mm deep | No. | 1
21 | Excavate not exceeding 600 mm deep in soft intermediate
rock material for cabling and cable pipe trench including
bedding, backfilling, compaction and disposal of surplus
| material | m³ | 4
22 | Excavate not exceeding 600 mm deep in hard rock for and
cabling and cable pipe trench including bedding, backfilling,
| compaction and disposal of surplus material | m³ | 1
SLEEVES
23 | 100 mm PVC sleeves | m | 18
24 | 100 mm long radius bend | No. | 2
25 | 50 mm PVC sleeves | m | 55
26 | 50 mm PVC long radius bend | No. | 6
27 | 50 mm galvanised sleeves | m | 13
28 | 50 mm long radius bend | No. | 2
| Carried Forward to Collection Page |  |  | R
Electrical Installation
Item
No. | STORM DAMAGE - EXISTING BLOCK B |  | Quantity | Rate | Amount
R
LIGHTING AND SMALL POWER
Thin walled hot dipped galvanised conduits
29 | 20mm diameter surface mounted on brickwork | m | 62
30 | 20mm diameter fixed on timber rafters | m | 155
Thin walled PVC conduits
31 | 20mm diameter chased in brickwork | m | 12
32 | 20mm diameter fixed on timber rafters | m | 25
CONDUIT BOXES AND FITTINGS
33 | 100 x 100 x 100/50 mm Deep hot dipped galvanised
box for 20mm diameter conduit in brick or concrete
| walls including conduit ends and cover | No. | 15
34 | 65 mm Round hot dipped galvanised box for 20mm
diameter steel conduit in brick or concrete walls or
| ceiling void including conduit ends and cover | No. | 34
35 | P8000 Trunking inclusive of PVC cover | m | 35
CONDUCTORS
PVC insulated stranded copper conductors drawn into
wireways
36 | 2.5mm² | m | 420
37 | 4mm² | m | 260
LIGHT SWITCHES, SWITCHED SOCKET OUTLETS ETC.
Switches etc. complete with cover plates fixed in flush
boxes
38 | 20A surface mounted 1 lever 1 way light switch | No. | 5
39 | 20A surface mounted Three-pin & Euro combo switch
| socket outlet with cover plate | No. | 10
R
Carried Forward to Collection Page
Electrical Installation
Item
No. | STORM DAMAGE - EXISTING BLOCK B |  | Quantity | Rate | Amount
R
LUMINAIRES AND EQUIPMENT
Luminaires or equipment complete with lamps,
connections etc. mounted in position
40 | Type A - 2 x 35W T5 Eurolux / Osram open channel
fluorescent light fitting with telescopic lamp holder
| complete with electronic control gear | No. | 20
41 | Type B - Swannlite/Magnet/Lihlelight or other approved
RML round bulkhead with 1 x PL26 Watt lamp complete
| with electronic control gear | No. | 10
42 | Type C - 2 x 35W T5 Vapour proof fluorescent light
| fitting complete with electronic control gear | No. | 1
43 | Photocells inclusive of enclosure | No. | 1
Carried Forward to Collection Page
R
Electrical Installation
Item
No. | STORM DAMAGE - EXISTING BLOCK C |  | Quantity | Rate | Amount
R
LIGHTING AND SMALL POWER
Thin walled hot dipped galvanised conduits
44 | 20mm diameter surface mounted on brickwork | m | 51
45 | 20mm diameter fixed on timber rafters | m | 126
Thin walled PVC conduits
46 | 20mm diameter chased in brickwork | m | 23
47 | 20mm diameter fixed on timber rafters | m | 31
CONDUIT BOXES AND FITTINGS
48 | 100 x 100 x 100/50 mm Deep hot dipped galvanised
box for 20mm diameter conduit in brick or concrete
| walls including conduit ends and cover | No. | 12
49 | 65 mm Round hot dipped galvanised box for 20mm
diameter steel conduit in brick or concrete walls or
| ceiling void including conduit ends and cover | No. | 26
50 | P8000 Trunking inclusive of PVC cover | m | 33
CONDUCTORS
PVC insulated stranded copper conductors drawn into
wireways
51 | 2.5mm² | m | 436
52 | 4mm² | m | 243
LIGHT SWITCHES, SWITCHED SOCKET OUTLETS ETC.
Switches etc. complete with cover plates fixed in flush
boxes
53 | 20A surface mounted 1 lever 1 way light switch | No. | 4
54 | 20A surface mounted Three-pin & Euro combo switch
| socket outlet with cover plate | No. | 8
Carried Forward to Collection Page
R
Electrical Installation
Item
No. | STORM DAMAGE - EXISTING BLOCK C |  | Quantity | Rate | Amount
R
LUMINAIRES AND EQUIPMENT
Luminaires or equipment complete with lamps,
connections etc. mounted in position
55 | Type A - 2 x 35W T5 Eurolux / Osram open channel
fluorescent light fitting with telescopic lamp holder
| complete with electronic control gear | No. | 16
56 | Type B - Swannlite/Magnet/Lihlelight or other approved
RML round bulkhead with 1 x PL26 Watt lamp complete
| with electronic control gear | No. | 10
57 | Type C - 2 x 35W T5 Vapour proof fluorescent light
| fitting complete with electronic control gear | No. | 1
58 | Photocells inclusive of enclosure | No. | 1
Carried Forward to Collection Page
R
Electrical Installation
Item
No. | STORM DAMAGE - EXISTING BLOCK D |  | Quantity | Rate | Amount
R
LIGHTING AND SMALL POWER
Thin walled hot dipped galvanised conduits
59 | 20mm diameter surface mounted on brickwork | m | 51
60 | 20mm diameter fixed on timber rafters | m | 126
Thin walled PVC conduits
61 | 20mm diameter chased in brickwork | m | 23
62 | 20mm diameter fixed on timber rafters | m | 31
CONDUIT BOXES AND FITTINGS
63 | 100 x 100 x 100/50 mm Deep hot dipped galvanised
box for 20mm diameter conduit in brick or concrete
| walls including conduit ends and cover | No. | 12
64 | 65 mm Round hot dipped galvanised box for 20mm
diameter steel conduit in brick or concrete walls or
| ceiling void including conduit ends and cover | No. | 26
65 | P8000 Trunking inclusive of PVC cover | m | 33
CONDUCTORS
PVC insulated stranded copper conductors drawn into
wireways
66 | 2.5mm² | m | 436
67 | 4mm² | m | 243
LIGHT SWITCHES, SWITCHED SOCKET OUTLETS ETC.
Switches etc. complete with cover plates fixed in flush
boxes
68 | 20A surface mounted 1 lever 1 way light switch | No. | 4
69 | 20A surface mounted Three-pin & Euro combo switch
| socket outlet with cover plate | No. | 8
Carried Forward to Collection Page
R
Electrical Installation
Item
No. | STORM DAMAGE - EXISTING BLOCK D |  | Quantity | Rate | Amount
R
LUMINAIRES AND EQUIPMENT
Luminaires or equipment complete with lamps,
connections etc. mounted in position
70 | Type A - 2 x 35W T5 Eurolux / Osram open channel
fluorescent light fitting with telescopic lamp holder
| complete with electronic control gear | No. | 16
71 | Type B - Swannlite/Magnet/Lihlelight or other approved
RML round bulkhead with 1 x PL26 Watt lamp complete
| with electronic control gear | No. | 10
72 | Type C - 2 x 35W T5 Vapour proof fluorescent light
| fitting complete with electronic control gear | No. | 1
73 | Photocells inclusive of enclosure | No. | 1
Carried Forward to Collection Page
R
Electrical Installation
Item
No. | STORM DAMAGE - EXISTING BLOCK E |  | Quantity | Rate | Amount
R
LIGHTING AND SMALL POWER
Thin walled hot dipped galvanised conduits
74 | 20mm diameter surface mounted on brickwork | m | 35
75 | 20mm diameter fixed on timber rafters | m | 115
Thin walled PVC conduits
76 | 20mm diameter chased in brickwork | m | 18
77 | 20mm diameter fixed on timber rafters | m | 26
CONDUIT BOXES AND FITTINGS
78 | 100 x 100 x 100/50 mm Deep hot dipped galvanised
box for 20mm diameter conduit in brick or concrete
| walls including conduit ends and cover | No. | 10
79 | 65 mm Round hot dipped galvanised box for 20mm
diameter steel conduit in brick or concrete walls or
| ceiling void including conduit ends and cover | No. | 22
80 | P8000 Trunking inclusive of PVC cover | m | 24
CONDUCTORS
PVC insulated stranded copper conductors drawn into
wireways
81 | 2.5mm² | m | 356
82 | 4mm² | m | 190
LIGHT SWITCHES, SWITCHED SOCKET OUTLETS ETC.
Switches etc. complete with cover plates fixed in flush
boxes
83 | 20A surface mounted 1 lever 1 way light switch | No. | 3
84 | 20A surface mounted Three-pin & Euro combo switch
| socket outlet with cover plate | No. | 6
Carried Forward to Collection Page
R
Electrical Installation
Item
No. | STORM DAMAGE - EXISTING BLOCK E |  | Quantity | Rate | Amount
R
LUMINAIRES AND EQUIPMENT
Luminaires or equipment complete with lamps,
connections etc. mounted in position
85 | Type A - 2 x 35W T5 Eurolux / Osram open channel
fluorescent light fitting with telescopic lamp holder
| complete with electronic control gear | No. | 12
86 | Type B - Swannlite/Magnet/Lihlelight or other approved
RML round bulkhead with 1 x PL26 Watt lamp complete
| with electronic control gear | No. | 10
87 | Type C - 2 x 35W T5 Vapour proof fluorescent light
| fitting complete with electronic control gear | No. | 1
88 | Photocells inclusive of enclosure | No. | 1
Carried Forward to Collection Page
R
Electrical Installation
Item
No. | STORM DAMAGE - EXISTING BLOCK F |  | Quantity | Rate | Amount
R
LIGHTING AND SMALL POWER
Thin walled hot dipped galvanised conduits
89 | 20mm diameter surface mounted on brickwork | m | 51
90 | 20mm diameter fixed on timber rafters | m | 126
Thin walled PVC conduits
91 | 20mm diameter chased in brickwork | m | 23
92 | 20mm diameter fixed on timber rafters | m | 31
CONDUIT BOXES AND FITTINGS
93 | 100 x 100 x 100/50 mm Deep hot dipped galvanised
box for 20mm diameter conduit in brick or concrete
| walls including conduit ends and cover | No. | 12
94 | 65 mm Round hot dipped galvanised box for 20mm
diameter steel conduit in brick or concrete walls or
| ceiling void including conduit ends and cover | No. | 26
95 | P8000 Trunking inclusive of PVC cover | m | 33
CONDUCTORS
PVC insulated stranded copper conductors drawn into
wireways
96 | 2.5mm² | m | 436
97 | 4mm² | m | 243
LIGHT SWITCHES, SWITCHED SOCKET OUTLETS ETC.
Switches etc. complete with cover plates fixed in flush
boxes
98 | 20A surface mounted 1 lever 1 way light switch | No. | 4
99 | 20A surface mounted Three-pin & Euro combo switch
| socket outlet with cover plate | No. | 8
Carried Forward to Collection Page
R
Electrical Installation
Item
No. | STORM DAMAGE - EXISTING BLOCK F |  | Quantity | Rate | Amount
R
LUMINAIRES AND EQUIPMENT
Luminaires or equipment complete with lamps,
connections etc. mounted in position
100 | Type A - 2 x 35W T5 Eurolux / Osram open channel
fluorescent light fitting with telescopic lamp holder
| complete with electronic control gear | No. | 16
101 | Type B - Swannlite/Magnet/Lihlelight or other approved
RML round bulkhead with 1 x PL26 Watt lamp complete
| with electronic control gear | No. | 10
102 | Type C - 2 x 35W T5 Vapour proof fluorescent light
| fitting complete with electronic control gear | No. | 1
103 | Photocells inclusive of enclosure | No. | 1
Carried Forward to Collection Page
R
Electrical Installation
Item
No. | STORM DAMAGE - EXISTING BLOCK G |  | Quantity | Rate | Amount
R
LIGHTING AND SMALL POWER
Thin walled hot dipped galvanised conduits
104 | 20mm diameter surface mounted on brickwork | m | 23
105 | 20mm diameter fixed on timber rafters | m | 76
Thin walled PVC conduits
106 | 20mm diameter chased in brickwork | m | 18
107 | 20mm diameter fixed on timber rafters | m | 27
CONDUIT BOXES AND FITTINGS
108 | 100 x 100 x 100/50 mm Deep hot dipped galvanised
box for 20mm diameter conduit in brick or concrete
| walls including conduit ends and cover | No. | 6
109 | 65 mm Round hot dipped galvanised box for 20mm
diameter steel conduit in brick or concrete walls or
| ceiling void including conduit ends and cover | No. | 16
| P8000 Trunking inclusive of PVC cover | m | 16
CONDUCTORS
PVC insulated stranded copper conductors drawn into
wireways
110 | 2.5mm² | m | 236
111 | 4mm² | m | 86
LIGHT SWITCHES, SWITCHED SOCKET OUTLETS ETC.
Switches etc. complete with cover plates fixed in flush
boxes
112 | 20A surface mounted 1 lever 1 way light switch | No. | 2
113 | 20A surface mounted Three-pin & Euro combo switch
| socket outlet with cover plate | No. | 4
Carried Forward to Collection Page
R
Electrical Installation
Item
No. | STORM DAMAGE - EXISTING BLOCK G |  | Quantity | Rate | Amount
R
LUMINAIRES AND EQUIPMENT
Luminaires or equipment complete with lamps,
connections etc. mounted in position
114 | Type A - 2 x 35W T5 Eurolux / Osram open channel
fluorescent light fitting with telescopic lamp holder
| complete with electronic control gear | No. | 8
115 | Type B - Swannlite/Magnet/Lihlelight or other approved
RML round bulkhead with 1 x PL26 Watt lamp complete
| with electronic control gear | No. | 8
116 | Type C - 2 x 35W T5 Vapour proof fluorescent light
| fitting complete with electronic control gear | No. | 1
117 | Photocells inclusive of enclosure | No. | 1
Carried Forward to Collection Page
R
Electrical Installation
Item | EXISTING INSTALLATION
No. |  |  | Quantity | Rate | Amount
| BLOCK B |  |  |  | R
Disconnect, make wiring safe and remove the following
118 | 20mm conduit | m | 201
119 | 2,5mm PVC insulated wire | m | 155
120 | 1,5mm PVC insulated wire | m | 279
121 | 65 mm dia. PVC conduit box | No. | 23
122 | 100 x 100/50 conduit box and cover | No. | 10
123 | Light switch | No. | 5
124 | Switch socket outlets | No. | 10
125 | 2 x 58 Watt surface light fitting | No. | 30
126 | Bulkhead light fitting | No. | 8
127 | Distribution Board | No. | 1
BLOCK C
Disconnect, make wiring safe and remove the following
128 | 20mm conduit | m | 189
129 | 2,5mm PVC insulated wire | m | 141
130 | 1,5mm PVC insulated wire | m | 259
131 | 65 mm dia. PVC conduit box | No. | 21
132 | 100 x 100/50 conduit box and cover | No. | 10
133 | Light switch | No. | 4
134 | Switch socket outlets | No. | 8
135 | 2 x 58 Watt surface light fitting | No. | 24
136 | Bulkhead light fitting | No. | 8
137 | Alarm Siren | No. | 1
138 | Distribution Board | No. | 1
Carried Forward to Collection Page
R
Electrical Installation
Item
No. | EXISTING INSTALLATION |  | Quantity | Rate | Amount
R
BLOCK D
Disconnect, make wiring safe and remove the following
139 | 20mm conduit | m | 189
140 | 2,5mm PVC insulated wire | m | 141
141 | 1,5mm PVC insulated wire | m | 259
142 | 65 mm dia. PVC conduit box | No. | 21
143 | 100 x 100/50 conduit box and cover | No. | 10
144 | Light switch | No. | 4
145 | Switch socket outlets | No. | 8
146 | 2 x 58 Watt surface light fitting | No. | 24
147 | Bulkhead light fitting | No. | 8
148 | Distribution Board | No. | 1
BLOCK E
Disconnect, make wiring safe and remove the following
149 | 20mm conduit | m | 171
150 | 2,5mm PVC insulated wire | m | 134
151 | 1,5mm PVC insulated wire | m | 243
152 | 65 mm dia. PVC conduit box | No. | 17
153 | 100 x 100/50 conduit box and cover | No. | 8
154 | Light switch | No. | 3
155 | Switch socket outlets | No. | 6
156 | 2 x 58 Watt surface light fitting | No. | 18
157 | Bulkhead light fitting | No. | 8
158 | Distribution Board | No. | 1
Carried Forward to Collection Page
R
Electrical Installation
Item
No. | EXISTING INSTALLATION |  | Quantity | Rate | Amount
R
BLOCK F
Disconnect, make wiring safe and remove the following
159 | 20mm conduit | m | 189
160 | 2,5mm PVC insulated wire | m | 141
161 | 1,5mm PVC insulated wire | m | 259
162 | 65 mm dia. PVC conduit box | No. | 21
163 | 100 x 100/50 conduit box and cover | No. | 10
164 | Light switch | No. | 4
165 | Switch socket outlets | No. | 8
166 | 2 x 58 Watt surface light fitting | No. | 24
167 | Bulkhead light fitting | No. | 8
168 | Distribution Board | No. | 1
BLOCK G
Disconnect, make wiring safe and remove the following
169 | 20mm conduit | m | 156
170 | 2,5mm PVC insulated wire | m | 118
171 | 1,5mm PVC insulated wire | m | 223
172 | 65 mm dia. PVC conduit box | No. | 14
173 | 100 x 100/50 conduit box and cover | No. | 5
174 | Light switch | No. | 2
175 | Switch socket outlets | No. | 2
176 | 2 x 58 Watt surface light fitting | No. | 10
177 | Bulkhead light fitting | No. | 4
178 | Distribution Board | No. | 1
Carried Forward to Collection Page
R
Electrical Installation
Item
No. | LIGHTNING PROTECTION |  | Quantity | Rate | Amount
R
BLOCK B C, D, E, F & G
179 | Undertake soil resistivity test, witnessed by the
Engineer inclusive of submitting a typed test
| report/certificate | Item
180 | 10 mm² aluminium conductor | m | 42
181 | 50 mm² PVC insulated aluminium earth wire | m | 156
182 | Bonding of earth tails to sheet trusses/roof
| sheeting/tiles | No. | 34
183 | Supply and install 25 mm galvanised conduit | m | 119
184 | Supply and install stainless steel lugs | No. | 68
185 | Supply and install stainless steel bolts and nuts | No. | 68
186 | Supply and install stop cork box | No. | 34
187 | 1,8 m earth spike | No. | 44
TESTING AND CERTIFICATE OF COMPLIANCE
188 | Allow for testing of the complete installation to be
witnessed by the Electrical Engineer, including the
issue of SABS Certificate of Compliance of Earthing
Systems, Annexures of recorded test results and "As
| Built" drawings as specified. | Item
Carried Forward to Collection Page
R
Electrical Installation
ELECTRICAL WORK
|  |  | Page |  | Amount
| COLLECTION PAGE |  | No |  | R
| Total brought forward from Page No |  | 2
| Total brought forward from Page No |  | 7
| Total brought forward from Page No |  | 8
| Total brought forward from Page No |  | 9
| Total brought forward from Page No |  | 10
| Total brought forward from Page No |  | 11
| Total brought forward from Page No |  | 12
| Total brought forward from Page No |  | 13
| Total brought forward from Page No |  | 14
| Total brought forward from Page No |  | 15
| Total brought forward from Page No |  | 16
| Total brought forward from Page No |  | 17
| Total brought forward from Page No |  | 18
| Total brought forward from Page No |  | 19
| Total brought forward from Page No |  | 20
| Total brought forward from Page No |  | 21
| Total brought forward from Page No |  | 22
| Total brought forward from Page No |  | 23
| Total brought forward from Page No |  | 24
| Total brought forward from Page No |  | 25
R
Electrical Installation