## Cover Page
CONTRACT NO : RFP046/2025
CONSTRUCTION OF PHASE 1 ROOIWAL WWTW
*
PART 3: ELECTRICAL AND MECHANICAL EAST WORKS BOQ

## F Summary
CITY OF TSHWANE
CONTRACT NO : RFP046/2025
CONSTRUCTION OF PHASE 1 ROOIWAL WWTW EAST WORKS
ELECTRICAL AND MECHANICAL FINAL SUMMARY
ITEM | DESCRIPTION | AMOUNT
1 | PRELIMINARY AND GENERAL | 0
2 | PROVISIONAL SUMS | 0
3 | ELECTRICAL WORKS | 0
4 | MECHANCAL WORKS | 0
| SUBTOTAL (A) | 0
The following sums will be under the sole control of the Engineer and may be deducted in part or full.
| ADD CONTINGENCY 10% | 0
| SUBTOTAL (B) | 0
| Contractor to allow 5% for CIDB Built Programme | 0
| SUBTOTAL (C) | 0
EPWP TRAINING
| Allow for EPWP Training | 1000000
| SUBTOTAL Excl VAT | 0
| ADD VAT (15%) | 0
TOTAL CARRIED TO FORM OF OFFER |  | 0

## 1_PGS (hidden)
CITY OF TSHWANE
CONTRACT NO : RFP208/2024
CONSTRUCTION OF PHASE 1 ROOIWAL WWTW
ELECTRICAL AND MECHANICAL SECTION: P&GS
ITEM | DESCRIPTION | UNIT | QTY | RATES | AMOUNT
The supply, installation, testing, commissioning and a 52 week defects liability period in accordance with this bill of material, Local Supply Authority's by-laws & regulations, National Building Regulations, detailed electrical specification, SANS 10142-1: 2003 (Code of Practice), Occupational Health and Safety Act, General Conditions of Contract and drawings listed in the detailed specification.
1 | Schedule No 1 Preliminary and General Fixed charge items
1.1 | Site establishment Allow for site establishment, and for storage of plant, materials and equipment including protection thereof. | Item | 1
1.2 | Site disestablishment Allow for the demolishing and removal of the site camp upon completion of the contract. | Item | 1
1.3 | Commissioning and testing Supply all test equipment and labour for testing and commissioning of the final installation. | Item | 1
1.4 | Guarantee Allow for a guarantee period of 12 months against defect in equipment, material and workmanship, but wear and tear and normal maintenance excluded. | Item | 1
1.5 | Additional fixed charge items Any additional item(s) that the tenderer may wish to detail and price. | Item | 1
1.6 | AS BUILT DRAWINGS The marking - up of "As Built" drawings during the contract to ensure that accurate "As Built" drawings are submitted to the Engineer at the end of the contract. | Sum | 1
1.7 | Training of Staff | Sum | 1
1.71 | Contractor to allow for CIDB Built Programme | Prov Sum | 1 | 5%
1.8 | OPERATING & MAINTENANCE MANUALS Compilation of an O & M manual | Sum | 1
1.9 | .14 Provisional sum for salary of CLO and travel assistance of Project Steering Committee Members appointed by Employer | Prov Sum | 1 | 300000 | 0
1.1 | Profit and attendance on item 1.10 | % |  | 300000
TOTAL CARRIED FORWARD |  |  |  |  | 0
BROUGHT FORWARD |  |  |  |  | 0
1.11 | Occupational Health and Safety:
1.11.1 | General safety obligations
1.11.1 | Mandatory Signage / Road signs | Sum | 1
1.11.2 | Safety Poster including Acts & Regulations | Sum | 1
1.11.3 | Safety office / shed or container | Month | 12
1.11.4 | Allowance for toilets (Gender specific) | Each | 1
1.11.5 | Lay down & storage areas | Sum | 1
1.11.6 | Employee eating area | Sum | 1
1.11.7 | Hand washing & sanitizing stations | Sum | 1
1.12 | Safety Planning
1.12.1 | Safety file and Risk Assessment | Sum | 1
1.12.2 | Health and safety plan | Sum | 1
1.12.6 | Medical assessment of employees (Entrance & Exit) & Vaccines for for employees working within sewer | Sum | 1
1.12.7 | Fall Protection Plan | Sum | 1
1.12.8 | Traffic Management Plan | Sum | 1
1.13 | Safety Personnel
1.13.2 | Construction safety officer (Full time) | Month | 12
1.14 | OHS Training
1.14.1 | Safety Representative Training | Sum | 1
1.14.2 | First Aid Training | Sum | 1
1.14.3 | Construction vehicle operators | Sum | 1
1.14.4 | Working at Heights training | Sum | 1
1.14.5 | Fire fighting training | Sum | 1
1.15 | Personal Protective Equipment (PPE)
1.15.1 | Work overalls - Reflective Conti suits (Min 2 pairs each) | Sum | 1
1.15.2 | Safety Shoes | Sum | 1
1.15.3 | Gum Boots | Sum | 1
1.15.4 | Hardhats | Sum | 1
1.15.5 | Reflective vests | Sum | 1
1.15.6 | Ear Plugs | Sum | 1
1.15.7 | Ear Muffs | Sum | 1
1.15.8 | Full body Safety Harness (Double lanyard) | Sum | 1
TOTAL CARRIED FORWARD |  |  |  |  | 0
BROUGHT FORWARD |  |  |  |  | 0
1.15.9 | Life Lines | Sum | 1
1.15.10 | Dust / Cloth Masks | Sum | 1
1.15.11 | Eye protection (Safety Glasses) | Sum | 1
1.15.12 | Hand Protection (Gloves) 100pcs | Sum | 1
1.15.13 | Barricade Netting (1 x 50m) | Sum
1.15.14 | Edge protection material & equipment | Sum
1.15.15 | Fire Extinguishers (9kg) | Sum
1.15.16 | First Aid box (GR3 kit). Including refill kits required. | Sum
1.15.17 | Spill kit (120litre) | Sum
1.15.18 | Lock out items (locks, tags,safes, etc..) | Sum
1.15.19 | Emergency air siren | Sum
1.15.20 | Rescue equipment | Sum
| TOTAL CARRIED FORWARD TO FINAL SUMMARY PAGE |  |  |  | 0

## Preliminaries
CITY OF TSHWANE
CONTRACT NO : RFP046/2025
CONSTRUCTION OF PHASE 1 ROOIWAL WWTW NORTH AND WEST WORKS
ELECTRICAL AND MECHANICAL FINAL SUMMARY
ITEM | DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
SCHEDULED ESTABLISHMENT, OVERHEADS & INCIDENTAL COSTS
NOTES
The supply, installation, testing, commissioning and a 52 week defects liability period in accordance with this bill of material, Local Supply Authority's by-laws & regulations, National Building Regulations, detailed electrical specification, SANS 10142-1: 2003 (Code of Practice), Occupational Health and Safety Act, General Conditions of Contract and drawings listed in the detailed specification.
1.The rates and/or prices for items scheduled in this Section under the headings - ONCE-OFF ESTABLISHMENT COST - DE-ESTABLISHMENT COST and - ONGOING OPERATIONAL AND OVERHEAD COST include everything to cover the Contractor's direct costs, overheads, profit and expenses required for all risks, liabilities and obligations in terms of this contract. (excluding VAT) 2.The rates and/or prices for items scheduled in this section under the heading "INCIDENTAL EXPENDITURE PROVISIONS" must be prised in this framework tender. The Contractor hereby agrees that these rates will be used for compensation event cost calculation and pricing where applicable instead of Defined Cost, unless otherwise decided by the Employer, at the Employer's sole discretion. Any items not priced are deemed to be included 3.Lump sum prices in this section are fixed for the contract, and are not subject to adjustment in compensation event assessments.
1 | ONCE-OFF ESTABLISHMENT COST
(Claimable for payment upon completion of all related activities associated with each item)
Contractual Requirements
1.1 | Compliance with all clauses of the Contract and Works Information | Sum | 1 |  | 0
1.2 | Compliance with the law, regulations and by laws | Sum | 1 |  | 0
1.3 | Compliance of tender participation goal in respect of local resources as per items in annexure 5 | Sum | 1 |  | 0
1.4 | Compliance with the stipulations of the Environmental Specification | Sum | 1 |  | 0
1.5 | Insurance and liabilities | Sum | 1 |  | 0
1.6 | Performance bond | Sum | 1 |  | 0
Establish Facilities on the Site
Facilities for Project Manager
1.7 | Air conditioned office accommodation with suitable tables and chairs for meetings to be held on the site | Sum | 1 |  | 0
1.8 | Contract name board - Refer to WCG Guidelines | Sum | 1 |  | 0
Facilities for Contractor
1.9 | Offices (shared with Project Manager) | Sum | 1 |  | 0
1.1 | Workshops | Sum | 1 |  | 0
1.11 | Laboratories | Sum | 1 |  | 0
1.12 | Ablutions and latrine facilities | Sum | 1 |  | 0
1.13 | Tools and equipment | Sum | 1 |  | 0
1.14 | Water supply | Sum | 1 |  | 0
1.15 | Electricity supply | Sum | 1 |  | 0
1.16 | Communication | Sum | 1 |  | 0
DE-ESTABLISHMENT COST
1.17 | Costs for complete removal of site establishment and restoration of the site to the Project Mangers satisfaction at the end of the contract: | Sum | 1 |  | 0
2 | ONGOING OPERATIONAL AND OVERHEAD COST
Claimable for payment as a time-related cost during execution of the contract
Contractual Requirements
2.1 | Compliance with all clauses of the Contract and Works Information | Sum | 1 |  | 0
2.2 | Compliance with the law, regulations and by laws | Sum | 1 |  | 0
2.3 | Compliance of tender participation goal in respect of local resources as per items in annexure 5 | Sum | 1 |  | 0
2.4 | Insurance and liabilities | Sum | 1 |  | 0
2.5 | Performance bond | Sum | 1 |  | 0
2.6 | Facilities for Project Manager
2.7 | Air conditioned office accommodation with suitable tables and chairs for meetings to be held on the site | Sum | 1 |  | 0
2.8 | Facilities for Contractor
2.9 | Offices (shared with Project Manager) | Sum | 1 |  | 0
2.1 | Workshops | Sum | 1 |  | 0
2.11 | Laboratories | Sum | 1 |  | 0
2.12 | Ablutions and latrine facilities | Sum | 1 |  | 0
2.13 | Tools and equipment | Sum | 1 |  | 0
2.14 | Water supply | Sum | 1 |  | 0
2.15 | Electricity supply | Sum | 1 |  | 0
2.16 | Communication | Sum | 1 |  | 0
2.17 | Provisional sum for salary for the Resident Engineer | sum | 1 | 2673000 | 2673000
2.18 | Profit and attendance on item 2.17 | % | 0 | 2673000 | 0
2.19 | Company and head office costs | Sum | 1 |  | 0
3 | INCIDENTAL EXPENDITURE PROVISIONS
The quantities listed are included for tender evaluation purposes only, and do not reflect actual quantities envisaged for the project. The rates offered shall apply for compensation event pricing for the duration of the contract where applicable
All compensation event costs related to people are allocated according to the breakdown of categories below (or nearest matching category, if no exact description match). The following rate adjustments will apply for after hours work: Weekdays after hours and Saturdays - Rate X 1.5 Sundays and Public Holidays - Rate X 2
3.1 | Contract/Project Manager | Days | 0 | 0 | Rate
3.2 | Site Manager | Days | 0 | 0 | rate
3.3 | Safety Officer | Days | 0 | 0 | rate
3.4 | Site Foreman (General Supervisor) | Days | 0 | 0 | rate
3.5 | Foreman (Supervisor) | Days | 0 | 0 | rate
3.6 | Administrative clerk | Days | 0 | 0 | rate
3.7 | Skilled Artisan | Days | 0 | 0 | rate
3.8 | Semi-Skilled Artisan | Days | 0 | 0 | rate
4 | PROJECT SPECIFIC PRELIMINARIES
4.1 | Workshop Drawings | Sum | 1 |  | 0
4.2 | As built Drawings | Sum | 1 |  | 0
4.3 | Training of Staff | Sum | 1 |  | 0
4.4 | Operating and Maintenance Manuals | Sum | 1 |  | 0
4.5 | One year Maintenance Guarantee | Sum | 1 |  | 0
5 | Occupational Health and Safety |  | 0
0
5.1 | General safety obligations |  | 0
0
5.1.1 | Mandatory Signage / Road signs | Sum | 1 |  | 0
0
5.1.2 | Safety Poster including Acts & Regulations | Sum | 1 |  | 0
0
5.1.3 | Safety office / shed or container for the duration of the contract | Sum | 1 |  | 0
0
5.1.4 | Allowance for toilets (Gender specific) | Each | 3 |  | 0
0
5.1.5 | Lay down & storage areas | Sum | 1 |  | 0
0
5.1.6 | Employee eating area | Sum | 1 |  | 0
0
5.1.7 | Hand washing & sanitizing stations | Sum | 1 |  | 0
5.1.8 | Compliance with the Occupational Health and Safety Act, Construction Regulations and Health and Safety Specification for the duration of the contract | Sum | 1 |  | 0
0
5.2 | Safety Planning |  | 0
0
5.2.1 | Safety file and Risk Assessment | Sum | 1 |  | 0
0
5.2.2 | Health and safety plan | Sum | 1 |  | 0
0
5.2.3 | Medical assessment of employees (Entrance & Exit) & Vaccines for for employees working within sewer | Sum | 1 |  | 0
0
5.2.4 | Fall Protection Plan | Sum | 1 |  | 0
0
5.2.5 | Traffic Management Plan | Sum | 1 |  | 0
0
5.3 | Safety Personnel |  | 0
0
5.3.1 | Construction safety officer (Full time) | Month | 12 |  | 0
0
5.3.2 | Work overalls - Reflective Conti suits (Min 2 pairs each) | Each | 50 |  | 0
|  |  | 0 |  | 0
5.3.3 | Safety Shoes | Each | 50 |  | 0
|  |  | 0 |  | 0
5.3.4 | Gum Boots | Each | 50 |  | 0
|  |  | 0 |  | 0
5.3.5 | Hardhats | Each | 50 |  | 0
|  |  | 0 |  | 0
5.3.6 | Reflective vests | Each | 50 |  | 0
|  |  | 0 |  | 0
5.3.7 | Ear Plugs (100's) | Box | 10 |  | 0
|  |  | 0 |  | 0
5.3.8 | Ear Muffs | Each | 50 |  | 0
|  |  | 0 |  | 0
5.3.9 | Full body Safety Harness (Double lanyard) | Each | 2 |  | 0
|  |  | 0 |  | 0
5.3.10 | Life Lines | Each | 2 |  | 0
|  |  | 0 |  | 0
5.3.11 | Dust / Cloth Masks (100s) | Box | 100 |  | 0
|  |  | 0 |  | 0
5.3.12 | Eye protection (Safety Glasses) | Each | 60 |  | 0
|  |  | 0 |  | 0
5.3.13 | Hand Protection (Gloves) 100pcs | Bulk | 50 |  | 0
|  |  | 0 |  | 0
5.3.14 | Barricade Netting (1 x 50m) | Sum | 1 |  | 0
|  |  | 0 |  | 0
5.3.15 | Edge protection material & equipment | Sum | 1 |  | 0
|  |  | 0 |  | 0
5.3.16 | Fire Extinguishers (9kg) | Each | 2 |  | 0
|  |  | 0 |  | 0
5.3.17 | First Aid box (GR3 kit). Including refill kits required. | Each | 2 |  | 0
|  |  | 0 |  | 0
5.3.18 | Spill kit (120litre) | Each | 2 |  | 0
0
5.3.19 | Lock out items (locks, tags,safes, etc..) | Sum | 1 |  | 0
0
5.3.20 | Emergency air siren | Each | 2 |  | 0
0
5.3.21 | Rescue equipment | Sum | 1 |  | 0
| Total Preliminaries |  |  |  | 0

## Provisional Sums
CITY OF TSHWANE
CONTRACT NO : RFP047/2025
CONSTRUCTION OF PHASE 1 ROOIWAL WWTW NORTH AND WEST WORKS
ELECTRICAL AND MECHANICAL FINAL SUMMARY
| Description | Unit | Qty | Rate | Total
Bill No 3:Provisionals and Generals
3 | Provisionals
3.1 | Provision for Fire Safety Related Work | sum | 1 | 200000 | 200000
3.2 | Provision for Ventilation Related Work | sum | 1 | 350000 | 350000
3.3 | Provision for Building Related Work | sum | 1 | 2500000 | 2500000
3.4 | Provision for Access ,dewatering and drainage related Services Related Work | sum | 1 | 800000 | 800000
3.5 | Provision for Cleaning,sludge and Waste Disposal Work | sum | 1 | 1200000 | 1200000
3.6 | Lightning Protection System | sum | 1 | 35000 | 35000
3.7 | MV Equipment & Switchgear Repair & Upgrade | sum | 1 | 125000 | 125000
3.8 | Rerfubishment of 16 X Highmast Light Structures & Kiosks | sum | 1 | 320000 | 320000
3.9 | Provisional sum for salary of CLO and travel assistance of Project Steering Committee Members appointed by Employer | sum | 1 | 96000 | 96000
3.1 | Profit and attendance on item 3.9 | % |  | 96000
17 | Provision for Repairs and moving of existing services to be confirmed onsite | sum | 1 | 1600000 | 1600000
Subtotal Provisionals

## Electrical Summary
CITY OF TSHWANE
CONTRACT NO : RFP046/2025
CONSTRUCTION OF PHASE 1 ROOIWAL WWTW NORTH AND WEST WORKS
ELECTRICAL SUMMARY
SCHEDULE | DESCRIPTION | TOTAL | TOTAL
|  | LABOUR | MATERIAL
Schedule 1: | East Works Electrical | 0 | 0
Total Labour and Material
TOTAL CARRIED FORWARD TO FINAL SUMMARY PAGE |  |  | 0

## East Works
CITY OF TSHWANE
CONTRACT NO : RFP046/2025
CONSTRUCTION OF PHASE 1 ROOIWAL WWTW NORTH AND WEST WORKS
ELECTRICAL
PRICES
ITEM | DESCRIPTION |  | EST | UNIT | RATES | TOTAL | TOTAL
|  | UNIT | QTY | LABOUR | MATERIAL | LABOUR | MATERIAL
3 | Schedule No 3 EAST WORKS
3.1 | 300A, 30kA three pole circuit breaker and cradle to be installed into existing mini substation. | No | 1 |  |  | 0 | 0
3.2 | Manufacture, supply, off loading and installation of the Inlet Works IP66 Stainless Steel MCC including commissioning as detailed in the specifications and drawings. | No | 1 |  |  | 0 | 0
3.3 | Manufacture, supply, off loading and installation of the Inlet Works IP66 Stainless Steel MCC including commissioning as detailed in the specifications and drawings to cater for 2 x Mechanical Screens, 2 x Conyeros, PLC, Local DB& 2x Compressors ) | No | 1 |  |  | 0 | 0
3.4 | Refurbish and rewire of the existing MCC in Plant Room including commissioning as detailed in the specifications and drawings. | No | 1 |  |  | 0 | 0
3.5 | DIFFERENTIAL ULTRASONIC LEVEL DETECTOR: (Inlet Works in & Outflow)
a | FDU92 level sensor including 20m of cable. | No | 2 |  |  | 0 | 0
b | 304 stainless steel support bracket for the sensor head. | No | 2 |  |  | 0 | 0
c | FMU90 ultrasonic level transmitter. | No | 2 |  |  | 0 | 0
d | Programming of the ultrasonic level transmitter. | No | 2 |  |  | 0 | 0
e | FEB for the transmitter including terminals, surge arrestors, circuit breaker & stainless steel pedestal. | No | 2 |  |  | 0 | 0
3.6 | Refurbish and rewire of the existing Clarifier Bridge elecrical works mechanism including commissioning by rewiring and reequiping with new motors, emergency Stop/Start Stations, Welding Plug | No | 1 |  |  | 0 | 0
3.3 | LV CABLE PVC/SWA/PVC copper conductor cables strapped to cable ladders. (trenches, sleeves and cable terminations measured elsewhere):
a | 95mm2 x 4 core (MCC / DB supply) | m | 280 |  |  | 0 | 0
b | 70mm2 Kwena earthing conductor | m | 280 |  |  | 0 | 0
c | 16mm2 x 4 core ( panel) | m | 30 |  |  | 0 | 0
d | 6mm2 x 4 core (compressor cable) | m | 30 |  |  | 0 | 0
e | 6mm2 x 4 core (welding socket) | m | 10 |  |  | 0 | 0
f | 1.5mm2 x 3 core (emergency stop cable) | m | 30 |  |  | 0 | 0
3.4 | LV CABLE TERMINATION: PVC/SWA/PVC Exe corrosion guard cable glands (IP68) complete including conductor & earth termination, lugs, tapes, drilling etc
a | 95mm2 x 4 core (MCC / DB supply) | No | 2 |  |  | 0 | 0
b | 70mm2 Kwena earthing conductor | No | 2 |  |  | 0 | 0
c | 16mm2 x 4 core (control panel) | No | 2 |  |  | 0 | 0
d | 6mm2 x 4 core (compressor cable) | No | 6 |  |  | 0 | 0
e | 1.5mm2 x 3 core (emergency stop cable) | No | 4 |  |  | 0 | 0
3.5 | CABLE EXCAVATION:
a | Pickable material | m³ | 50 |  |  | 0 | 0
b | Soft Rock | m³ | 20 |  |  | 0 | 0
c | Hard Rock | m³ | 20 |  |  | 0 | 0
d | Backfilling & Compaction | m³ | 90 |  |  | 0 | 0
3.6 | CABLE ROUTE MARKERS: The supply and installation of concrete cable route markers | No | 10 |  |  | 0 | 0
3.7 | CABLE LADDER AND TRAY: OL55 duplex coating (exterior polyester) 3CR12 cable ladder including all accessories mounted to concrete slabs / walls.
a | 100mm cable ladder | m | 20 |  |  | 0 | 0
b | 100mm 90° bends | No | 4 |  |  | 0 | 0
c | 100mm duplex coating (exteria polyester) 3CR 12 cable tray. | m | 20 |  |  | 0 | 0
3.8 | LOCAL EMERGENCY STOP STATIONS:
a | Surface mounted IP65 emergency stop push buttons. | No | 12 |  |  | 0 | 0
b | Stainless Steel support stands for the above item. | No | 12 |  |  | 0 | 0
3.9 | Surface mounted 35A, 5 pin 3 phase welding socket including male plug. (to be mounted brick wall) | No | 1 |  |  | 0 | 0
LIGHTING AND SMALL POWER
3.1 | GALVANISED CONDUIT:
a | Surface mounted 20mm galvanised conduit including couplings, galvanised saddles and all accessories. | m | 110 |  |  | 0 | 0
c | Surface mounted round galvanised 20mm conduit boxes including galvanised cover plate. | No | 12 |  |  | 0 | 0
3.11 | PHOTO CELL:
a | Royce Thompson photo cell including conduit box. | No | 1 |  |  | 0 | 0
3.12 | WIRING PVC insulated copper conductors drawn into galvanised conduit:
a | 1.5mm2 | m | 200 |  |  | 0 | 0
b | 2.5mm2 | m | 300 |  |  | 0 | 0
3.13 | EARTH WIRING BCEW drawn into galvanised conduit:
a | 2.5mm2 | m | 180 |  |  | 0 | 0
3.14 | LUMINAIRES To be mounted to suspended ceilings and to brick walls:
a | 2 x 36W IP65 vapour proof LED luminaire complete Driver. | No | 6 |  |  | 0 | 0
b | 2 x 36W IP65 vapour proof LED Emergency Maintained luminaire complete Driver. | No | 4 |  |  | 0 | 0
3.15 | LIGHT SWITCHES Industrial surface mounted 16A single lever two way switch. | No | 2 |  |  | 0 | 0
TOTAL CARRIED FORWARD TO SUMMARY | [5 empty] | 0 | 0

## Mechanical Summary
CITY OF TSHWANE
CONTRACT NO : RFP046/2025
CONSTRUCTION OF PHASE 1 ROOIWAL WWTW NORTH AND WEST WORKS
MECHANICAL SUMMARY
SUMMARY
| Bill No 1-East Heating System | 0
| Bill No 2-Mechanical Refurbisment Work | 0
| Total Carried forward to Mechanical and Electrical Bill | 0

## Bill No 1
CITY OF TSHWANE
CONTRACT NO : RFP046/2025
CONSTRUCTION OF PHASE 1 ROOIWAL WWTW EAST WORKS
MECHANICAL
Item | Desription | Unit | Qty | Rate | Total
BILL NO 1:DIGESTER PLANT HEATING SYSTEM REFURBISHMENT
1 | Digesters
1.001 | Supply and Install 1200x900x12mm Stainless Steel Gr 304/316 Checker Plate inspect hole lid complete with lifting handles,pre-drilled mounting holes,high tensile bolts | ea | 1 | 0 | 0
1.002 | Remove existing 1200 x 900mm cast iron neck at the inspection hole and replace with a stainless steel 12mm x GR304/316 Stainless steel including welded flanged lip to fit new lit with pre-drilled holes.This should include removal and recasting concrete with the neck | ea | 1 | 0 | 0
1.003 | Replace the 800dia x 12mm cast iron lid for the mixer inlet hole complete with pre-drilled holes ,bolts and gasket | ea | 1 | 0 | 0
1.004 | Supply and Install 500dia x12mm mild steel steam injection hole lid complete with pipe extension to connect to the 65mm steam supply line.Retain the existing neck,replace all bolts and gasket. | ea | 1 | 0 | 0
1.005 | Replace Steam Injection line into the digester:65mm x sch80S | m | 7 | 0 | 0
1.006 | Replace all AC Piping from the methane gas outlet to the valve chamber with welded stainless steel GR304/316 :125mm x sch80S | ea | 15 | 0 | 0
1.007 | Remove ,recast and replace existing methane gas outlet cast iron neck and replace with stainless steel GR304/316 neck complete with lip flanges with pre-drilled holes and gasket to mount new lid:1100mm x 12mm | ea | 1 | 0 | 0
1.008 | Supply and Install new stainless steel dome lid for methane gas outlet dome complete with pre-drilled holes,bolts,washers and a flanged outlet to mount methane gas piping | ea | 1 | 0 | 0
1.009 | Remove existing and replace pressure and vacuum breather valve complete with 125mm inline deflagration flame arrester | ea | 1 | 0 | 0
1.01 | Derust and repaint all hand railings at the Digester plant including those liding to the ground level | sum | 1 | 0 | 0
1.011 | Shorten existing 225mm cast iron scum removal/overflow piping to required level | ea | 1 | 0 | 0
1.012 | Supply and Install 225mm mechanical flange adapter to create a flange connection to the cast iron piping | ea | 1 | 0 | 0
1.013 | supply 225mm loose removable flange with gasket,bolts ,nuts and washers (to be used during crust removal)_ | ea | 1 | 0 | 0
1.014 | Supply and instal steel handrails to fully enclose the digester tank valve chamber (5m x 7m) | ea | 1 | 0 | 0
1.015 | Refurbish 125mm methane gas isolating valve in the valve chamber | ea | 1 | 0 | 0
1.016 | Replace all 125mm AC Methane gas piping with welded stainless steel Sch80S Gr 304/316 piping including properly coupling the piping to underground AC Piping to the boiler plant | m | 7 | 0 | 0
1.017 | Supply and Install new thermocouple with Analogue gauge for local readout | ea | 1 | 0 | 0
| Digester 8 Subtotal to Bill Summary |  |  |  | 0
1.2 | Digester 9
1.201 | Supply and Install 1200x900x12mm Stainless Steel Gr 304/316 Checker Plate inspect hole lid complete with lifting handles,pre-drilled mounting holes,high tensile bolts | ea | 1 | 0 | 0
1.202 | Remove existing 1200 x 900mm cast iron neck at the inspection hole and replace with a stainless steel 12mm x GR304/316 Stainless steel including welded flanged lip to fit new lit with pre-drilled holes.This should include removal and recasting concrete with the neck | ea | 1 | 0 | 0
1.203 | Replace the 800dia x 12mm cast iron lid for the mixer inlet hole complete with pre-drilled holes ,bolts and gasket | ea | 1 | 0 | 0
1.204 | Supply and Install 500dia x12mm mild steel steam injection hole lid complete with pipe extension to connect to the 65mm steam supply line.Retain the existing neck,replace all bolts and gasket. | ea | 1 | 0 | 0
1.205 | Replace Steam Injection line into the digester:65mm x sch80S | m | 7 | 0 | 0
1.206 | Replace the 800dia x 12mm cast iron lid for the mixer inlet hole complete with pre-drilled holes ,bolts and gasket | ea | 1 | 0 | 0
1.207 | Replace all AC Piping from the methane gas outlet to the valve chamber with welded stainless steel GR304/316 :125mm x sch80S | ea | 15 | 0 | 0
1.208 | Remove ,recast and replace existing methane gas outlet cast iron neck and replace with stainless steel GR304/316 neck complete with lip flanges with pre-drilled holes and gasket to mount new lid:1100mm x 12mm | ea | 1 | 0 | 0
1.209 | Supply and Install new stainless steel dome lid for methane gas outlet dome complete with pre-drilled holes,bolts,washers and a flanged outlet to mount methane gas piping | ea | 1 | 0 | 0
1.21 | Remove existing and replace pressure and vacuum breather valve complete with 125mm inline deflagration flame arrester | ea | 1 | 0 | 0
1.211 | Derust and repaint all hand railings at the Digester plant including those liding to the ground level | sum | 1 | 0 | 0
1.212 | Shorten existing 225mm cast iron scum removal/overflow piping to required level | ea | 1 | 0 | 0
1.213 | Supply and Install 225mm mechanical flange adapter to create a flange connection to the cast iron piping | ea | 1 | 0 | 0
1.214 | supply 225mm loose removable flange with gasket,bolts ,nuts and washers (to be used during crust removal)_ | ea | 1 | 0 | 0
1.215 | Supply and instal steel handrails to fully enclose the digester tank valve chamber (5m x 7m) | ea | 1 | 0 | 0
1.216 | Refurbish 125mm methane gas isolating valve in the valve chamber | ea | 1 | 0 | 0
1.217 | Replace all 125mm AC Methane gas piping with welded stainless steel Sch80S Gr 304/316 piping including properly coupling the piping to underground AC Piping to the boiler plant | m | 7 | 0 | 0
1.218 | Supply and Install new thermocouple with Analogue gauge for local readout | ea | 1 | 0 | 0
| Digester 9 Subtotal to Bill Summary |  |  |  | 0
1.3 | Digester 10
1.301 | Supply and Install 1200x900x12mm Stainless Steel Gr 304/316 Checker Plate inspect hole lid complete with lifting handles,pre-drilled mounting holes,high tensile bolts | ea | 1 | 0 | 0
1.302 | Remove existing 1200 x 900mm cast iron neck at the inspection hole and replace with a stainless steel 12mm x GR304/316 Stainless steel including welded flanged lip to fit new lit with pre-drilled holes.This should include removal and recasting concrete with the neck | ea | 1 | 0 | 0
1.303 | Replace the 800dia x 12mm cast iron lid for the mixer inlet hole complete with pre-drilled holes ,bolts and gasket | ea | 1 | 0 | 0
1.304 | Supply and Install 500dia x12mm mild steel steam injection hole lid complete with pipe extension to connect to the 65mm steam supply line.Retain the existing neck,replace all bolts and gasket. | ea | 1 | 0 | 0
1.305 | Replace Steam Injection line into the digester:65mm x sch80S | m | 7 | 0 | 0
1.306 | Replace the 800dia x 12mm cast iron lid for the mixer inlet hole complete with pre-drilled holes ,bolts and gasket | ea | 1 | 0 | 0
1.307 | Replace all AC Piping from the methane gas outlet to the valve chamber with welded stainless steel GR304/316 :125mm x sch80S | ea | 15 | 0 | 0
1.308 | Remove ,recast and replace existing methane gas outlet cast iron neck and replace with stainless steel GR304/316 neck complete with lip flanges with pre-drilled holes and gasket to mount new lid:1100mm x 12mm | ea | 1 | 0 | 0
1.309 | Supply and Install new stainless steel dome lid for methane gas outlet dome complete with pre-drilled holes,bolts,washers and a flanged outlet to mount methane gas piping | ea | 1 | 0 | 0
1.31 | Remove existing and replace pressure and vacuum breather valve complete with 125mm inline deflagration flame arrester | ea | 1 | 0 | 0
1.311 | Derust and repaint all hand railings at the Digester plant including those liding to the ground level | sum | 1 | 0 | 0
1.312 | Shorten existing 225mm cast iron scum removal/overflow piping to required level | ea | 1 | 0 | 0
1.313 | Supply and Install 225mm mechanical flange adapter to create a flange connection to the cast iron piping | ea | 1 | 0 | 0
1.314 | supply 225mm loose removable flange with gasket,bolts ,nuts and washers (to be used during crust removal)_ | ea | 1 | 0 | 0
1.315 | Supply and instal steel handrails to fully enclose the digester tank valve chamber (5m x 7m) | ea | 1 | 0 | 0
1.316 | Refurbish 125mm methane gas isolating valve in the valve chamber | ea | 1 | 0 | 0
1.317 | Replace all 125mm AC Methane gas piping with welded stainless steel Sch80S Gr 304/316 piping including properly coupling the piping to underground AC Piping to the boiler plant | m | 7 | 0 | 0
1.318 | Supply and Install new thermocouple with Analogue gauge for local readout | ea | 1 | 0 | 0
| Digester 10 Subtotal to Bill Summary |  |  |  | 0
1.4 | Digester 11
1.401 | Supply and Install 1200x900x12mm Stainless Steel Gr 304/316 Checker Plate inspect hole lid complete with lifting handles,pre-drilled mounting holes,high tensile bolts | ea | 1 | 0 | 0
1.402 | Remove existing 1200 x 900mm cast iron neck at the inspection hole and replace with a stainless steel 12mm x GR304/316 Stainless steel including welded flanged lip to fit new lit with pre-drilled holes.This should include removal and recasting concrete with the neck | ea | 1 | 0 | 0
1.403 | Replace the 800dia x 12mm cast iron lid for the mixer inlet hole complete with pre-drilled holes ,bolts and gasket | ea | 1 | 0 | 0
1.404 | Supply and Install 500dia x12mm mild steel steam injection hole lid complete with pipe extension to connect to the 65mm steam supply line.Retain the existing neck,replace all bolts and gasket. | ea | 1 | 0 | 0
1.405 | Replace Steam Injection line into the digester:65mm x sch80S | m | 7 | 0 | 0
1.406 | Replace the 800dia x 12mm cast iron lid for the mixer inlet hole complete with pre-drilled holes ,bolts and gasket | ea | 1 | 0 | 0
1.407 | Replace all AC Piping from the methane gas outlet to the valve chamber with welded stainless steel GR304/316 :125mm x sch80S | ea | 15 | 0 | 0
1.408 | Remove ,recast and replace existing methane gas outlet cast iron neck and replace with stainless steel GR304/316 neck complete with lip flanges with pre-drilled holes and gasket to mount new lid:1100mm x 12mm | ea | 1 | 0 | 0
1.409 | Supply and Install new stainless steel dome lid for methane gas outlet dome complete with pre-drilled holes,bolts,washers and a flanged outlet to mount methane gas piping | ea | 1 | 0 | 0
1.41 | Remove existing and replace pressure and vacuum breather valve complete with 125mm inline deflagration flame arrester | ea | 1 | 0 | 0
1.411 | Derust and repaint all hand railings at the Digester plant including those liding to the ground level | sum | 1 | 0 | 0
1.412 | Shorten existing 225mm cast iron scum removal/overflow piping to required level | ea | 1 | 0 | 0
1.413 | Supply and Install 225mm mechanical flange adapter to create a flange connection to the cast iron piping | ea | 1 | 0 | 0
1.414 | supply 225mm loose removable flange with gasket,bolts ,nuts and washers (to be used during crust removal)_ | ea | 1 | 0 | 0
1.415 | Supply and instal steel handrails to fully enclose the digester tank valve chamber (5m x 7m) | ea | 1 | 0 | 0
1.416 | Refurbish 125mm methane gas isolating valve in the valve chamber | ea | 1 | 0 | 0
1.417 | Replace all 125mm AC Methane gas piping with welded stainless steel Sch80S Gr 304/316 piping including properly coupling the piping to underground AC Piping to the boiler plant | m | 7 | 0 | 0
1.418 | Supply and Install new thermocouple with Analogue gauge for local readout | ea | 1 | 0 | 0
| Digester 11 Subtotal to Bill Summary |  |  |  | 0
1.5 | Digester 12
1.501 | Supply and Install 1200x900x12mm Stainless Steel Gr 304/316 Checker Plate inspect hole lid complete with lifting handles,pre-drilled mounting holes,high tensile bolts | ea | 1 | 0 | 0
1.502 | Remove existing 1200 x 900mm cast iron neck at the inspection hole and replace with a stainless steel 12mm x GR304/316 Stainless steel including welded flanged lip to fit new lit with pre-drilled holes.This should include removal and recasting concrete with the neck | ea | 1 | 0 | 0
1.503 | Replace the 800dia x 12mm cast iron lid for the mixer inlet hole complete with pre-drilled holes ,bolts and gasket | ea | 1 | 0 | 0
1.504 | Supply and Install 500dia x12mm mild steel steam injection hole lid complete with pipe extension to connect to the 65mm steam supply line.Retain the existing neck,replace all bolts and gasket. | ea | 1 | 0 | 0
1.505 | Replace Steam Injection line into the digester:65mm x sch80S | m | 7 | 0 | 0
1.506 | Replace the 800dia x 12mm cast iron lid for the mixer inlet hole complete with pre-drilled holes ,bolts and gasket | ea | 1 | 0 | 0
1.507 | Replace all AC Piping from the methane gas outlet to the valve chamber with welded stainless steel GR304/316 :125mm x sch80S | ea | 15 | 0 | 0
1.508 | Remove ,recast and replace existing methane gas outlet cast iron neck and replace with stainless steel GR304/316 neck complete with lip flanges with pre-drilled holes and gasket to mount new lid:1100mm x 12mm | ea | 1 | 0 | 0
1.509 | Supply and Install new stainless steel dome lid for methane gas outlet dome complete with pre-drilled holes,bolts,washers and a flanged outlet to mount methane gas piping | ea | 1 | 0 | 0
1.51 | Remove existing and replace pressure and vacuum breather valve complete with 125mm inline deflagration flame arrester | ea | 1 | 0 | 0
1.511 | Derust and repaint all hand railings at the Digester plant including those liding to the ground level | sum | 1 | 0 | 0
1.512 | Shorten existing 225mm cast iron scum removal/overflow piping to required level | ea | 1 | 0 | 0
1.513 | Supply and Install 225mm mechanical flange adapter to create a flange connection to the cast iron piping | ea | 1 | 0 | 0
1.514 | supply 225mm loose removable flange with gasket,bolts ,nuts and washers (to be used during crust removal)_ | ea | 1 | 0 | 0
1.515 | Supply and instal steel handrails to fully enclose the digester tank valve chamber (5m x 7m) | ea | 1 | 0 | 0
1.516 | Refurbish 125mm methane gas isolating valve in the valve chamber | ea | 1 | 0 | 0
1.517 | Replace all 125mm AC Methane gas piping with welded stainless steel Sch80S Gr 304/316 piping including properly coupling the piping to underground AC Piping to the boiler plant | m | 7 | 0 | 0
1.518 | Supply and Install new thermocouple with Analogue gauge for local readout | ea | 1 | 0 | 0
| Digester 12 Subtotal to Bill Summary |  |  |  | 0
1.6 | Digester 13
1.601 | Supply and Install 1200x900x12mm Stainless Steel Gr 304/316 Checker Plate inspect hole lid complete with lifting handles,pre-drilled mounting holes,high tensile bolts | ea | 1 | 0 | 0
1.602 | Remove existing 1200 x 900mm cast iron neck at the inspection hole and replace with a stainless steel 12mm x GR304/316 Stainless steel including welded flanged lip to fit new lit with pre-drilled holes.This should include removal and recasting concrete with the neck | ea | 1 | 0 | 0
1.603 | Replace the 800dia x 12mm cast iron lid for the mixer inlet hole complete with pre-drilled holes ,bolts and gasket | ea | 1 | 0 | 0
1.604 | Supply and Install 500dia x12mm mild steel steam injection hole lid complete with pipe extension to connect to the 65mm steam supply line.Retain the existing neck,replace all bolts and gasket. | ea | 1 | 0 | 0
1.605 | Replace Steam Injection line into the digester:65mm x sch80S | m | 7 | 0 | 0
1.606 | Replace the 800dia x 12mm cast iron lid for the mixer inlet hole complete with pre-drilled holes ,bolts and gasket | ea | 1 | 0 | 0
1.607 | Replace all AC Piping from the methane gas outlet to the valve chamber with welded stainless steel GR304/316 :125mm x sch80S | ea | 15 | 0 | 0
1.608 | Remove ,recast and replace existing methane gas outlet cast iron neck and replace with stainless steel GR304/316 neck complete with lip flanges with pre-drilled holes and gasket to mount new lid:1100mm x 12mm | ea | 1 | 0 | 0
1.609 | Supply and Install new stainless steel dome lid for methane gas outlet dome complete with pre-drilled holes,bolts,washers and a flanged outlet to mount methane gas piping | ea | 1 | 0 | 0
1.61 | Remove existing and replace pressure and vacuum breather valve complete with 125mm inline deflagration flame arrester | ea | 1 | 0 | 0
1.611 | Derust and repaint all hand railings at the Digester plant including those liding to the ground level | sum | 1 | 0 | 0
1.612 | Shorten existing 225mm cast iron scum removal/overflow piping to required level | ea | 1 | 0 | 0
1.613 | Supply and Install 225mm mechanical flange adapter to create a flange connection to the cast iron piping | ea | 1 | 0 | 0
1.614 | supply 225mm loose removable flange with gasket,bolts ,nuts and washers (to be used during crust removal)_ | ea | 1 | 0 | 0
1.615 | Supply and instal steel handrails to fully enclose the digester tank valve chamber (5m x 7m) | ea | 1 | 0 | 0
1.616 | Refurbish 125mm methane gas isolating valve in the valve chamber | ea | 1 | 0 | 0
1.617 | Replace all 125mm AC Methane gas piping with welded stainless steel Sch80S Gr 304/316 piping including properly coupling the piping to underground AC Piping to the boiler plant | m | 7 | 0 | 0
1.618 | Supply and Install new thermocouple with Analogue gauge for local readout | ea | 1 | 0 | 0
| Digester 13 Subtotal to Bill Summary |  |  |  | 0
1.7 | Digester 14
1.701 | Supply and Install 1200x900x12mm Stainless Steel Gr 304/316 Checker Plate inspect hole lid complete with lifting handles,pre-drilled mounting holes,high tensile bolts | ea | 1 | 0 | 0
1.702 | Remove existing 1200 x 900mm cast iron neck at the inspection hole and replace with a stainless steel 12mm x GR304/316 Stainless steel including welded flanged lip to fit new lit with pre-drilled holes.This should include removal and recasting concrete with the neck | ea | 1 | 0 | 0
1.703 | Replace the 800dia x 12mm cast iron lid for the mixer inlet hole complete with pre-drilled holes ,bolts and gasket | ea | 1 | 0 | 0
1.704 | Supply and Install 500dia x12mm mild steel steam injection hole lid complete with pipe extension to connect to the 65mm steam supply line.Retain the existing neck,replace all bolts and gasket. | ea | 1 | 0 | 0
1.705 | Replace Steam Injection line into the digester:65mm x sch80S | m | 7 | 0 | 0
1.706 | Replace the 800dia x 12mm cast iron lid for the mixer inlet hole complete with pre-drilled holes ,bolts and gasket | ea | 1 | 0 | 0
1.707 | Replace all AC Piping from the methane gas outlet to the valve chamber with welded stainless steel GR304/316 :125mm x sch80S | ea | 15 | 0 | 0
1.708 | Remove ,recast and replace existing methane gas outlet cast iron neck and replace with stainless steel GR304/316 neck complete with lip flanges with pre-drilled holes and gasket to mount new lid:1100mm x 12mm | ea | 1 | 0 | 0
1.709 | Supply and Install new stainless steel dome lid for methane gas outlet dome complete with pre-drilled holes,bolts,washers and a flanged outlet to mount methane gas piping | ea | 1 | 0 | 0
1.71 | Remove existing and replace pressure and vacuum breather valve complete with 125mm inline deflagration flame arrester | ea | 1 | 0 | 0
1.711 | Derust and repaint all hand railings at the Digester plant including those liding to the ground level | sum | 1 | 0 | 0
1.712 | Shorten existing 225mm cast iron scum removal/overflow piping to required level | ea | 1 | 0 | 0
1.713 | Supply and Install 225mm mechanical flange adapter to create a flange connection to the cast iron piping | ea | 1 | 0 | 0
1.714 | supply 225mm loose removable flange with gasket,bolts ,nuts and washers (to be used during crust removal)_ | ea | 1 | 0 | 0
1.715 | Supply and instal steel handrails to fully enclose the digester tank valve chamber (5m x 7m) | ea | 1 | 0 | 0
1.716 | Refurbish 125mm methane gas isolating valve in the valve chamber | ea | 1 | 0 | 0
1.717 | Replace all 125mm AC Methane gas piping with welded stainless steel Sch80S Gr 304/316 piping including properly coupling the piping to underground AC Piping to the boiler plant | m | 7 | 0 | 0
1.718 | Supply and Install new thermocouple with Analogue gauge for local readout | ea | 1 | 0 | 0
| Digester 14 Subtotal to Bill Summary |  |  |  | 0
1.8 | Digester 15
1.801 | Supply and Install 1200x900x12mm Stainless Steel Gr 304/316 Checker Plate inspect hole lid complete with lifting handles,pre-drilled mounting holes,high tensile bolts | ea | 1 | 0 | 0
1.802 | Remove existing 1200 x 900mm cast iron neck at the inspection hole and replace with a stainless steel 12mm x GR304/316 Stainless steel including welded flanged lip to fit new lit with pre-drilled holes.This should include removal and recasting concrete with the neck | ea | 1 | 0 | 0
1.803 | Replace the 800dia x 12mm cast iron lid for the mixer inlet hole complete with pre-drilled holes ,bolts and gasket | ea | 1 | 0 | 0
1.804 | Supply and Install 500dia x12mm mild steel steam injection hole lid complete with pipe extension to connect to the 65mm steam supply line.Retain the existing neck,replace all bolts and gasket. | ea | 1 | 0 | 0
1.805 | Replace Steam Injection line into the digester:65mm x sch80S | m | 7 | 0 | 0
1.806 | Replace the 800dia x 12mm cast iron lid for the mixer inlet hole complete with pre-drilled holes ,bolts and gasket | ea | 1 | 0 | 0
1.807 | Replace all AC Piping from the methane gas outlet to the valve chamber with welded stainless steel GR304/316 :125mm x sch80S | ea | 15 | 0 | 0
1.808 | Remove ,recast and replace existing methane gas outlet cast iron neck and replace with stainless steel GR304/316 neck complete with lip flanges with pre-drilled holes and gasket to mount new lid:1100mm x 12mm | ea | 1 | 0 | 0
1.809 | Supply and Install new stainless steel dome lid for methane gas outlet dome complete with pre-drilled holes,bolts,washers and a flanged outlet to mount methane gas piping | ea | 1 | 0 | 0
1.81 | Remove existing and replace pressure and vacuum breather valve complete with 125mm inline deflagration flame arrester | ea | 1 | 0 | 0
1.811 | Derust and repaint all hand railings at the Digester plant including those liding to the ground level | sum | 1 | 0 | 0
1.812 | Shorten existing 225mm cast iron scum removal/overflow piping to required level | ea | 1 | 0 | 0
1.813 | Supply and Install 225mm mechanical flange adapter to create a flange connection to the cast iron piping | ea | 1 | 0 | 0
1.814 | supply 225mm loose removable flange with gasket,bolts ,nuts and washers (to be used during crust removal)_ | ea | 1 | 0 | 0
1.815 | Supply and instal steel handrails to fully enclose the digester tank valve chamber (5m x 7m) | ea | 1 | 0 | 0
1.816 | Refurbish 125mm methane gas isolating valve in the valve chamber | ea | 1 | 0 | 0
1.817 | Replace all 125mm AC Methane gas piping with welded stainless steel Sch80S Gr 304/316 piping including properly coupling the piping to underground AC Piping to the boiler plant | m | 7 | 0 | 0
1.818 | Supply and Install new thermocouple with Analogue gauge for local readout | ea | 1 | 0 | 0
| Digester 15 Subtotal to Bill Summary |  |  |  | 0
1.9 | Methane Gas Flare Burner
1.901 | Isolate,Dismantle,safely relocate and reassemble the flare burner unit from the valve chamber to the designated area next to the steam boiler plant. | sum | 1 | 0 | 0
1.902 | Refurbish and Recommission Flare Burner | ea | 1 | 0 | 0
1.903 | Supply and Install Welded 100mm Sch80S stainless piping from the valve chamber to the new location of the flare burner.Stainless Steel piping to run overhead on existing platforms | m | 70 | 0 | 0
1.904 | Supply and install 100mm detonation flame arrestor | ea | 1 | 0 | 0
1.1 | Valve Chamber and Gas Holder |  |  | 0 | 0
1.101 | Clean 150mm Concealed AC Methane Gas Line | sum | 1 | 0 | 0
1.102 | Pressure Test 150mm AC Line | ea | 1 | 0 | 0
1.103 | Provision for Repairs as per pressure test report | m | 50 | 0 | 0
1.104 | Refurbish 150mm methane gas isolating valves | ea | 3 | 0 | 0
1.105 | replace 150mm inline deflagration frame arrestors | ea | 3 | 0 | 0
1.106 | replace 150mm corroded and AC Piping section in the valve chamber with welded stainless steel grade 304/316 including tees and couplings | m | 10 | 0 | 0
1.107 | Refurbish isolating valve to the gas holder | ea | 1 | 0 | 0
1.108 | Supply and install handrailings at the main valve chamber(7m x7m) | ea | 1 | 0 | 0
1.109 | Clean valve chamber and unblock all drains | ea | 1 | 0 | 0
1.11 | Replace AC overlflow pipe with Mild Steel piping :75mm | m | 4 | 0 | 0
1.111 | Refurbish Scour valve:150mm | ea | 1 | 0 | 0
1.112 | Replace Overflow Float and ball valve in the make up tank | ea | 1 | 0 | 0
1.113 | Corrosion Protection of the entire gas collection dome (13m diameter)in situ | sum | 1 | 0 | 0
1.114 | Refurbish guide rollers and frame columns of the gas collecting dome frame | ea | 8 | 0 | 0
1.115 | Replace all frame anchor bolts(4 per column x 8 columns) | ea | 8 | 0 | 0
1.116
1.117 | Flare Burner and Gas Holder Subtotal |  |  |  | 0
1.12 | Steam Piping
1.121 | Remove existing steam piping ,lagging,cladding,hangers and brackets from digester 8-15 and to the old steam boiler plant | m | 220 | 0 | 0
1.122 | Properly dispose of fiberglass insulation removed from the steam pipes | sum | 1 | 0 | 0
1.123 | Supply and Install 65mm Sch80 Welded steam piping including 25mm fibreglass insulation and 0.8mm Grade 304/316 Stainless Steel Cladding including bends,tees,reducers and Expansion Bellows .Use existing platforms for mounting steam piping but these excludes the mounting brackets | m | 160 | 0 | 0
1.124 | Supply and Install 65mm Globe valves for Isolating steam supply to Digesters 8-15 | ea | 8 | 0 | 0
1.125 | Supply and Install 80mm Sch80 Welded steam piping including 25mm fibreglass insulation and 0.8mm Grade 304/316 Stainless Steel Cladding including bends,tees,reducers and Expansion bellows.Use existing platforms for mounting steam piping but these excludes the mounting brackets | m | 90 | 0 | 0
1.126 | Supply and Install 65mm Steam Non Return Valves | ea | 8 | 0 | 0
1.127 | Supply and install 20mm complete steam trap arrangement | ea | 4 | 0 | 0
1.128 | Supply and Install 100mm Sch80 Welded steam piping including 25mm fibreglass insulation and 0.8mm Grade 304/316 Stainless Steel Cladding including bends,tees,reducers and Expansion bellows.Use existing platforms for mounting steam piping but these excludes the mounting brackets | m | 25 | 0 | 0
1.129 | Supply and Install new 200mm inline deflagration flame arrestor outside the boiler plant | ea | 1 | 0 | 0
1.13 | Old Steam Generator/Boiler Plant
1.131 | Conduct and submit a comprehensive Non Destructive Testing Report to evaluale the structural integrity of the old biogas Cyclotherm Steam Boiler(Serial 2800…33/Type CE…2800) | ea | 1 | 0 | 0
1.132 | Relocate the boiler from the old boiler plant to the new boiler plant ,this includes dismantling,safe transportation and reinstallation | ea | 1 | 0 | 0
1.133 | Based on the NDT Findings,perform necessary repairs to restore the boiler to full operational status.Preparation and repairs works to meet or exceed standards required for a 36-Month Interval Inspection.All repair activities to be conducted at the new boiler plant | ea | 1 | 0 | 0
1.134 | Hydrostatic Pressure Testing and Approved Inspection Authority Certification of the Cyclothem Boiler | ea | 1 | 0 | 0
| Steam Piping and Generator Subtotal |  |  |  | 0
1.14 | New Steam Generator/Boiler Plant
1.141 | Conduct and submit a comprehensive Non Destructive Testing Report to evaluale the structural integrity of the new uncommissioned biogas Cyclotherm Steam Boiler(Serial 2800…33/Type CE…2800) | ea | 1 | 0 | 0
1.142 | Based on the NDT Findings,perform necessary repairs to restore the boiler to full operational status.Preparation and repairs works to meet or exceed standards required for a 36-Month Interval Inspection.All repair activities to be conducted at the new boiler plant | ea | 1 | 0 | 0
1.143 | Hydrostatic Pressure Testing post repairs and Approved Inspection Authority Certification (AIA) | ea | 1 | 0 | 0
1.144 | Supply,install and commissioning of new water treatment plant | ea | 1 | 0 | 0
1.145 | Supply , Install and commissionng of new water filtration and softening plant for the feedwater system | ea | 1 | 0 | 0
1.146 | Twelve Months Supply of Water Treatment Chemicals and brine for water softening plant | ea | 12 | 0 | 0
1.147 | Supply and Install 50mm Galvanised feedwater water piping including accompaning fittings from the feedwater tanks to the two commissioned boilers | m | 20 | 0 | 0
1.148 | Commission feedwater tanks and Pumps | ea | 1 | 0 | 0
1.149 | Supply and install 100dia Steam piping including 25mm fibreglass lagging and 0.8mm GR304/316 stainless steel piping from the boiler outlet to the supply header and from the header to connect to the outside lines | m | 20 | 0 | 0
1.15 | 100dia Steam Globe valves for steam supply Isolation | ea | 1 | 0 | 0
1.151 | Supply and Install 50mm galvanised water piping including fittings from the gas collecting dome to the new boiler plant | m | 30 | 0 | 0
1.152 | Supply ,install and commission 2 x 48kg LPG Gas bank outside the the new boiler plant including piping to the boilers,changeover switch pressure testing,commisioning and certification | sum | 1 | 0 | 0
| New Steam Generator Subtotal |  |  |  | 0
Subtotals
1.1 | Digester 8 |  |  |  | 0
1.2 | Digester 9 |  |  |  | 0
1.3 | Digester 10 |  |  |  | 0
1.4 | Digester 11 |  |  |  | 0
1.5 | Digester 12 |  |  |  | 0
1.6 | Digester 13 |  |  |  | 0
1.7 | Digester 14 |  |  |  | 0
1.8 | Digester 15 |  |  |  | 0
1.9 | Flare Burner and Gas Holder |  |  |  | 0
2 | Steam Piping and Generator |  |  |  | 0
2.1 | New Steam Generator |  |  |  | 0
| Mechanical East Works Heating System carried to Summary(Excl Vat) |  |  |  | 0

## Bill No 2
CITY OF TSHWANE
CONTRACT NO : RFP046/2025
CONSTRUCTION OF PHASE 1 ROOIWAL WWTW EAST WORKS
MECHANICAL
Mechanical
Section | Rooiwal East
| Description | Unit | Qty | Rate | Total
BILL No 2:East Mechanical Refurbishment Work
2.1 | Inlet Screens
2.101 | Refurbish inlet sluice gates: This should include removal, disassembly, corrosion treatment, lubrication, handwheel maintenance, refubishment of guides and all associated seals. | ea | 3 |  | 0
2.102 | Provision of for Derusting and Corrosion protection of inlet works mentis grid hand railing. | sum | 1 |  | 0
2.103 | Corrosion protection of all the floor gratings at the inlet works | sum | 1 |  | 0
2.104 | Supply and installation of 1500mm x 1500mm fine expanded metal or grating downstream of the three rung steps at inlet channel number 2. | ea | 1 |  | 0
2.105 | Refurbishment of the mechanical inlet screen no 1 including repairs to the chain rollers, sprockets, supply of new proximity switch, new chains, damaged floating bars, damaged scraper bucket, replacement of the rakes with double sided rakes, service of the screen motor and replacement of the stainless steel four rakes at the scrapper. | ea | 1 |  | 0
2.106 | Supply and installation of a new mechanical inlet screen to readily fit into the 1700mm wide inlet channel number 2. The mechanical screen must be supplied as per the provided specification and similar to the mechanical screen on inlet 1. The screen must come complete with motor and accessories to empty into the horizontal screw. | ea | 1 |  | 0
2.107 | Provision for major service of the removed screen on inlet channel no 2. | ea | 1 |  | 0
2.108 | Refurbish horizontal screw including changing of the bearings and modification at the bearing block to prevent ingress of water into the bearings. | ea | 1 |  | 0
2.109 | Supply and Install rising (inclined) screw conveyor including the replacement of shaft ( Ø50mm x 4m), flight and modifications to the bearing blocks to prevent ingress of water as per specification provided. | ea | 1 |  | 0
2.11 | Refurbish Outlet sluice gates: This includes removal, disassembly, corrosion treatment, lubrication, handwheel maintenance, refurbishment of guide, and all associated seals. | ea | 3 |  | 0
2.111 | Supply and install of plain stainless steel identification plates at the inlet screens.(130mm x35mm x1mm Thick must include punching of ID Codes with Stainless Steel wire crimp) | sum | 1 |  | 0
| Inlet Screens Subtotal |  |  |  | 0
2.2 | Degritter Chamber
2.201 | Refurbish Degritter Inlet sluice gates: This includes removal, disassembly, corrosion treatment, lubrication, handwheel maintenance, refurbishment of guides and all associated seals. | ea | 2 |  | 0
2.202 | Replacement of all the deflector plates (400mm × 200mm) at the degritter chamber. The plates to be corrosion protected. | ea | 26 |  | 0
2.203 | Removal, corrosion protection, painting, and reinstallation of the the mentis handrails at the Degritter Chambers. | ea | 1 |  | 0
2.204 | Corrosion Protection of the floor grating at the degritter chamber bridge 1200mm × 600mm in size. | ea | 4 |  | 0
2.205 | Supply and Installation of new mild steel and corrosion protected Grit scrapers as per specifications provided. | ea | 2 |  | 0
2.206 | Replacement of the grit scraper drive motor ( 0,75kW Motor). | ea | 1 |  | 0
2.207 | Refurbish grit scraper motor gearbox. | ea | 2 |  | 0
2.208 | Supply and Installation of new grit removal submissible pumps preferably HCP or equivalently approved (4 Pole Motor x Vortex Impellers with duty 16l/s@ 8m Head). | ea | 2 |  | 0
2.209 | Supply of flexible hose for degritter pumps (Ø80mm). | m | 30 |  | 0
2.21 | Supply and Installation of new gate valves for grit classifier piping (Ø100mm). | ea | 4 |  | 0
2.211 | Supply and installation of Non return valves for grit removal piping (Ø100mm). | ea | 2 |  | 0
2.212 | Replace Motor and Gearbox for the screw conveyor at the grit classifier 1 ( 0,75kW). | ea | 1 |  | 0
2.213 | Refurbish grit classifier No 1 including corrosion protection of the screw, changing of the Ø50mm bearings and modifications at the bearing blocks to prevent ingress of water into bearings, and refurbishment of the wear lining. Refurb and paint grit classifier return line. | ea | 1 |  | 0
2.214 | Refurbish grit classifier No 2. | ea | 1 |  | 0
2.215 | Derust, repair, corrosion protection and painting of the Ø150mm return piping from the grit classifiers 1 and 2 including replacement of gaskets and rusted bolts at the flanges. | m | 20 |  | 0
2.216 | Supply and Install a new screw conveyor at grit classifier no 2 as per the specification provided. This includes a new shaft, flight, linings, bearings, and wear lining. | ea | 1 |  | 0
2.217 | De-rust and painting of manual lifting equipment at the grit chambers. | ea | 2 |  | 0
2.218 | De-rust and paint the degritter bridge beams. | ea | 2 |  | 0
2.219 | Supply and install of plain stainless steel identification plates at the degritter chambers.(130mm x35mm x1mm Thick must include punching of ID Codes with Stainless Steel wire crimp) | sum | 1 |  | 0
| Degritter Chambers Subtotal |  |  |  | 0
2.3 | Primary Settling Treatment
2.301 | Refurbish Sluice gates at the PST Division Chambers. | ea | 4 |  | 0
2.302 | Refurbish Sluice gates at the PST Inlets. | ea | 8 |  | 0
2.303 | Replace all the asbestos scum baffles at the Primary settling tanks with Stainless Steel baffles preferably Grade 304 or better approved. | ea | 8 |  | 0
2.304 | Replace the entire scum remover mechanicals including the motor, gearbox, scraper arm, scraper rubber, draw off line, and scraper bridge. | ea | 8 |  | 0
2.305 | Supply and Installation of New Tip Valves x Ø200mm made from 304 Stainless Steel. | ea | 8 |  | 0
2.306 | Refurbishment of scum isolating vlaves (Ø450mm). | ea | 8 |  | 0
2.307 | Refurbish all IQ12 × 81Nm Rotork Actuators for Primary Sludge Draw off. | ea | 8 |  | 0
2.308 | Supply and installation of lateral supports for the shafts connecting the draw off valves and the rotork actuators. | ea | 8 |  | 0
2.309 | Refurbish the fine screens 1: The refurbishment should include the changing of the bottom bearing for the bottom shaft, top bearing for the top shaft, replacement of the broken stainless steel racks (four off ) and conveyor shaft. New rakes must be double raked with teeth opening of 6mm and bar gaps 10mm. | ea | 1 |  | 0
2.31 | Refurbish the fine screens 2: The refurbishment should include the changing of the bottom bearing for the bottom shaft, top bearing for the top shaft, replacement of the 0,5kW Gearbox and motor, replacement of the broken stainless steel racks (four off ) and conveyor shaft. New rakes must be double raked with teeth opening of 6mm and bar gaps 10mm. | ea | 1 |  | 0
2.311 | Supply of new fine screen bins as per specificaton and drawings. | ea | 1 |  | 0
2.312 | Supply and install of plain stainless steel identification plates at the primary settling tanks.(130mm x35mm x1mm Thick must include punching of ID Codes with Stainless Steel wire crimp) | sum | 1 |  | 0
| Primary Settling Tanks Subtotal |  |  |  | 0
2.4 | Primary Sludge Pump Station
2.401 | Refurbish the Manual Isolation Ø300mm valves into the Primary Sludge Pump station. This includes the bypass valve between sump 1 and 2. | ea | 3 |  | 0
2.402 | Refurbish Manual Suction Isolating valves for the sludge pumps x Ø300mm. | ea | 5 |  | 0
2.403 | Supply and install HCP or equivalently approved submersible (1,5kW x 2-Pole Motor x Vortex Impleller with Duty 3l/s @ 14m Head) drainage pump including float switch and piping to discharge (Allow for Ø50mm pipe x 6m of mild steel piping) back into the primary sump. | ea | 1 |  | 0
2.404 | Derust, corrosion treatment, and painting of the 2T beam inside the plant room. | ea | 1 |  | 0
2.405 | Load Test and certify 2T Single Beam lifting equipment. | ea | 1 |  | 0
2.406 | Supply and install of plain stainless steel identification plates at the primary sludge Pumpstation.(130mm x35mm x1mm Thick must include punching of ID Codes with Stainless Steel wire crimp) | sum | 1 |  | 0
2.407 | Fines Screen No 1: Refurbish bars, rake, top and bottom bearings. Rakes to be double-raked. Replace motor and gearbox. Rake teeth opening of 6mm, bars shall have a gap of 10mm. | each | 1 |  | 0
2.408 | Fines Screen No 2: Refurbish the fine screen including the replacement of the conveyor motor and gearbox. | each | 1 |  | 0
| Primary Sludge Pumpstation Subtotal |  |  |  | 0
2.5 | Anaerobic Digester Plants
2.501 | Replace Mixing Pumps (Vaughan Model HE8N100SB × 1900m3/h @ 39m Head) complete with Motor . | ea | 3 |  | 0
2.502 | Refurbish Inflow Isolating Valves (Ø400mm). | ea | 8 |  | 0
2.503 | Refurbish Manual Outflow Isolating Valves (Ø400mm). | ea | 8 |  | 0
2.504 | Refurbish Manual Supernetant Water Isolating Valves (Ø80mm). | ea | 24 |  | 0
2.505 | Refurbish Mixing Valves (Ø250mm ). | ea | 24 |  | 0
2.506 | Refurbish Rotork actuators for the mixer Inlet valves. | ea | 8 |  | 0
2.507 | Derusting, corrosion protection and painting of all exposed piping and fittings at each digester tank. | ea | 8 |  | 0
2.508 | Refurbish sludge feed manifold Isolating valves (Ø400mm) | ea | 2 |  | 0
2.509 | Supply and install of plain stainless steel identification plates for the Anaerobic digester Plant. | sum | 1 |  | 0
2.51 | Piping Labeling at each Digestor Plant. | ea | 1 |  | 0
2.511 | Supply and install of plain stainless steel identification plates at the Anaerobic Digester Plant.(130mm x35mm x1mm Thick must include punching of ID Codes with Stainless Steel wire crimp) | sum | 1 |  | 0
| Anaerobic Digester Plant Subtotal |  |  |  | 0
2.6 | Digested Sludge Pump Station
2.601 | Refurbish the Gorman Rupp Ultra V6A60 pumps, including replacing missing components to restore the pump to full operation. | ea | 1 |  | 0
2.602 | Replace Gorman Rupp Ultra V6A60 Pump as per standard specification provided. | ea | 1 |  | 0
2.603 | Refurbish all manual suction and discharge valves (Ø225mm). | ea | 4 |  | 0
2.604 | Supply and install HCP or equivalently approved submersible (1,5kW x 2-Pole Motor x Vortex Impleller with Duty 3l/s @ 14m Head) drainage pump including float switch and piping to discharge (Allow for Ø50mm pipe x 6m of mild steel piping) back into the primary sump. | ea | 1 |  | 0
2.605 | Derust, corrosion treatment, and painting of the 2T beam inside the plantroom. | ea | 1 |  | 0
2.606 | Load Test and certify 2T Single Beam lifting equipment. | ea | 1 |  | 0
2.607 | Supply and install of plain stainless steel identification plates at the Digested Sludge Pump Station.(130mm x35mm x1mm Thick must include punching of ID Codes with Stainless Steel wire crimp) | sum | 1 |  | 0
2.608 | Refurbishment of Ø300mm inlet valves in situ at Digested sludge Pumpstation | ea | 2 |  | 0
| Digested Sludge Pumpstation |  |  |  | 0
2.7 | Trickling Bio Filters
2.701 | Refurbish Sluice Gates at the main dividing chambers. | ea | 8 |  | 0
2.702 | Refubish the dosing siphon cast iron dome which includes rust removal, corrosion treatment and coating. | ea | 8 |  | 0
2.703 | Replace dome pipe and fittings ( Ø60mm × Sch 80). | m | 64 |  | 0
2.704 | Supply and Install dome Supports(Minimum of 3 supports per dome required) | ea | 48 |  | 0
2.705 | Supply and Install Hand Stops at the Biofilter dividing Chambers. | ea | 16 |  | 0
2.706 | Quote to Strip and Refurbish biofilter centre columns. Refurbishment must include crannage removal, disassembly, assessment, replacement of top bearings, replacement of the bottom bushing, bottom centre housing, sandblasting, corrosion treatment, reassembly and reinstalling crannage. | ea | 8 |  | 0
2.707 | Provision for Replacement of the center columns. | ea | 8 |  | 0
2.708 | Replacement of cross wire ropes holding distribution piping including replacement of the turnbuckles. | ea | 64 |  | 0
2.709 | Replacement of wire ropes from the supporting rods including the replacement of turnbuckles | ea | 64 |  | 0
2.71 | Refurbish the scour valves (Ø125mm). | ea | 16 |  | 0
2.711 | Supply and install of plain stainless steel identification plates at the Biofilters.(130mm x35mm x1mm Thick must include punching of ID Codes with Stainless Steel wire crimp) | sum | 1 |  | 0
| Trickling Biofilters Subtotal |  |  |  | 0
2.8 | Ferri Dosing Plant
2.801 | Supply and Installation of a pre-assembled Dosseuro or equivalently approved Ferri Dosing plant with four duty peristaltic pumps @ 271l/h + one standby pump. New plant must come fully tested and precommissioned to connect only to the existing outlet piping. | sum | 1 |  | 0
2.802 | Replace all PVC Piping inside the plantroom. | sum | 1 |  | 0
2.803 | Integrity Test and Certification of existing Ferri Bulk Tanks including sealing off the gap between the tank bottom and the floor with concrete. | sum | 2 |  | 0
2.804 | Replace all the PVC Ferri Chloride piping from the refill points,to the ferri tanks and then to the ferri dosing plant (Ø50mm). | sum | 1 |  | 0
2.805 | Supply and install of plain stainless steel identification plates at the Ferri Dosing Tanks. | sum | 1 |  | 0
| Subtotal Ferri Dosing Plant |  |  |  | 0
2.9 | Humus Tanks
2.901 | Refurbish inlet sluice gates at the dividing chambers | ea | 16 |  | 0
2.902 | Replace all the asbestos scum baffles at the Primary settling tanks with Stainless Steel baffles preferably Grade 304 Or better approved. | ea | 12 |  | 0
2.903 | Supply of Towable Diesel Atlas Copco Compressor or equivalently approved better for unblocking sludge lines (200cfm minimum 7-12 Bars). | ea | 1 |  | 0
2.904 | Refurbish sludge and scum outlet valves (Ø100mm). | ea | 12 |  | 0
2.905 | Supply and install of plain stainless steel identification plates at the Humus Tanks.(130mm x35mm x1mm Thick must include punching of ID Codes with Stainless Steel wire crimp) | sum | 1 |  | 0
| Humus Tanks Subtotal |  |  |  | 0
2.1 | Effluent and Humus Pump Station
2.101 | Refurbish Isolating manual valves at the sump (Ø400mm). | ea | 4 |  | 0
2.102 | Refurbish Isolating manual humus valves at the humus pumps (Ø500mm). | ea | 4 |  | 0
2.103 | Paint all the humus piping inside the plantroom. | ea | 1 |  | 0
2.104 | Supply and Install 140l/s @ 25m Head End Suction Farmer Pump. | ea | 1 |  | 0
2.105 | Repair all leaks, treat corrosion and paint all piping at the farmers pumps (Ø600mm). | ea | 1 |  | 0
2.106 | Derust, corrosion protect and paint the 5T Single beams inside the plantroom. | ea | 2 |  | 0
2.107 | Certify and load Test beams and lifting equipment. | ea | 2 |  | 0
2.108 | Supply and install HCP or equivalently approved submersible (1,5kW x 2-Pole Motor x Vortex Impleller with Duty 3l/s @ 14m Head) drainage pump including float switch and piping to discharge (Allow for Ø50mm pipe x 6m of mild steel piping) back into the primary sump. | ea | 1 |  | 0
2.109 | Supply and install of plain stainless steel identification plates at the Effluent and Humus Pumpstation.(130mm x35mm x1mm Thick must include punching of ID Codes with Stainless Steel wire crimp) | sum | 1 |  | 0
| Subtotal Effluent Pumpstation |  |  |  | 0
Subtotals
2.1 | Inlet Screens Subtotal |  |  |  | 0
2.2 | Degritter Chambers Subtotal |  |  |  | 0
2.3 | Primary Settling Tanks Subtotal |  |  |  | 0
2.4 | Primary Sludge Pumpstation Subtotal |  |  |  | 0
2.5 | Anaerobic Digester Plant Subtotal |  |  |  | 0
2.6 | Digested Sludge Pumpstation |  |  |  | 0
2.7 | Trickling Biofilters Subtotal |  |  |  | 0
2.8 | Subtotal Ferri Dosing Plant |  |  |  | 0
2.9 | Humus Tanks Subtotal |  |  |  | 0
2.1 | Subtotal Effluent Pumpstation |  |  |  | 0
| Bill Total Carried to Summary |  |  |  | 0